## CermakA_0
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Grid_Electricity_Supplied_kWh_annual | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | NG_LifeCycle_Emissions_CO2 | Emissions_from_NG | LifeCycle_Emission_Reduction_Fraction | npv | lcc
Chicago | 388 | 513041 | 490374 | 0 | 1714 | 0 | 2077.939 | 10 | 13 | 3687.428 | 2554665 | 877.2916 | 877.2916 | 974.7684 | 21932.29 | 24369.21 | 0 | 0 | 10% | -101132.32 | 6066885.1
Chicago | 754 | 998657 | 954535 | 0 | 91344 | 0 | 29741.281 | 31 | 122 | 34150.076 | 2183538 | 779.8148 | 779.8148 | 974.7684 | 19495.37 | 24369.21 | 0 | 0 | 20% | -336370.57 | 6302123.35
Chicago | 1068 | 1414304 | 1351819 | 0 | 281393 | 0 | 122003.81 | 70 | 495 | 134090.409 | 1987469 | 682.338 | 682.338 | 974.7684 | 17058.45 | 24369.21 | 0 | 0 | 30% | -764792.53 | 6730545.31
Chicago | 1356 | 1795117 | 1715807 | 0 | 449974 | 0 | 254114.48 | 142 | 1014 | 269050.907 | 1807133 | 584.8612 | 584.8612 | 974.7684 | 14621.53 | 24369.21 | 0 | 0 | 40% | -1242357.5 | 7208110.28
Chicago | 1658 | 2194291 | 2097345 | 0 | 661268 | 0 | 375649.953 | 196 | 1487 | 387143.008 | 1650070 | 487.3844 | 487.3844 | 974.7684 | 12184.61 | 24369.21 | 0 | 0 | 50% | -1741898.23 | 7707651.02
Chicago | 1960 | 2594171 | 2479558 | 0 | 878667 | 0 | 500709.779 | 250 | 1970 | 504261.015 | 1498325 | 389.9072 | 389.9072 | 974.7684 | 9747.68 | 24369.21 | 0 | 0 | 60% | -2252717.14 | 8218469.92
Chicago | 2274 | 3010262 | 2877266 | 0 | 1128002 | 0 | 612353.665 | 294 | 2392 | 606327.854 | 1361342 | 292.4304 | 292.4304 | 974.7684 | 7310.76 | 24369.21 | 0 | 0 | 70% | -2771749.42 | 8737502.2
Chicago | 2581 | 3415949 | 3265029 | 0 | 1365079 | 0 | 735533.864 | 345 | 2855 | 718942.387 | 1223222 | 194.9536 | 194.9536 | 974.7684 | 4873.84 | 24369.21 | 0 | 0 | 80% | -3298381.3 | 9264134.09
Chicago | 2900 | 3838771 | 3669171 | 0 | 1634460 | 0 | 844780.461 | 391 | 3245 | 816071.382 | 1099304 | 97.4768 | 97.4768 | 974.7684 | 2436.92 | 24369.21 | 0 | 0 | 90% | -3831654.32 | 9797407.1
Chicago | 2900 | 3838771 | 3669171 | 0 | 1192888 | 0 | 1352662.97 | 682 | 5425 | 1363812.997 | 718877 | 0 | 0 | 974.7684 | 0 | 24369.21 | 0 | 0 | 100% | -4524826.16 | 10490578.94

## CermakA_1
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Grid_Electricity_Supplied_kWh_annual | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | NG_LifeCycle_Emissions_CO2 | Emissions_from_NG | LifeCycle_Emission_Reduction_Fraction | npv | lcc
Chicago | 388 | 513041 | 490374 | 0 | 1714 | 0 | 2077.939 | 10 | 13 | 3687.428 | 2554665 | 877.2916 | 877.2916 | 974.7684 | 21932.29 | 24369.21 | 0 | 0 | 0.1 | -101132.32 | 6066885.1
Chicago | 754 | 998657 | 954535 | 0 | 91344 | 0 | 29741.281 | 31 | 122 | 34150.076 | 2183538 | 779.8148 | 779.8148 | 974.7684 | 19495.37 | 24369.21 | 0 | 0 | 0.2 | -336370.57 | 6302123.35
Chicago | 1068 | 1414304 | 1351819 | 0 | 281393 | 0 | 122003.81 | 70 | 495 | 134090.409 | 1987469 | 682.338 | 682.338 | 974.7684 | 17058.45 | 24369.21 | 0 | 0 | 0.3 | -764792.53 | 6730545.31
Chicago | 1356 | 1795117 | 1715807 | 0 | 449974 | 0 | 254114.48 | 142 | 1014 | 269050.907 | 1807133 | 584.8612 | 584.8612 | 974.7684 | 14621.53 | 24369.21 | 0 | 0 | 0.4 | -1242357.5 | 7208110.28
Chicago | 1658 | 2194291 | 2097345 | 0 | 661268 | 0 | 375649.953 | 196 | 1487 | 387143.008 | 1650070 | 487.3844 | 487.3844 | 974.7684 | 12184.61 | 24369.21 | 0 | 0 | 0.5 | -1741898.23 | 7707651.02
Chicago | 1960 | 2594171 | 2479558 | 0 | 878667 | 0 | 500709.779 | 250 | 1970 | 504261.015 | 1498325 | 389.9072 | 389.9072 | 974.7684 | 9747.68 | 24369.21 | 0 | 0 | 0.6 | -2252717.14 | 8218469.92
Chicago | 2274 | 3010262 | 2877266 | 0 | 1128002 | 0 | 612353.665 | 294 | 2392 | 606327.854 | 1361342 | 292.4304 | 292.4304 | 974.7684 | 7310.76 | 24369.21 | 0 | 0 | 0.7 | -2771749.42 | 8737502.2
Chicago | 2581 | 3415949 | 3265029 | 0 | 1365079 | 0 | 735533.864 | 345 | 2855 | 718942.387 | 1223222 | 194.9536 | 194.9536 | 974.7684 | 4873.84 | 24369.21 | 0 | 0 | 0.8 | -3298381.3 | 9264134.09
Chicago | 2900 | 3838771 | 3669171 | 0 | 1634460 | 0 | 844780.461 | 391 | 3245 | 816071.382 | 1099304 | 97.4768 | 97.4768 | 974.7684 | 2436.92 | 24369.21 | 0 | 0 | 0.9 | -3831654.32 | 9797407.1
Chicago | 2900 | 3838771 | 3669171 | 0 | 1192888 | 0 | 1352662.97 | 682 | 5425 | 1363812.997 | 718877 | 0 | 0 | 974.7684 | 0 | 24369.21 | 0 | 0 | 1 | -4524826.16 | 10490578.94

## CermakA_2
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Grid_Electricity_Supplied_kWh_annual | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | NG_LifeCycle_Emissions_CO2 | Emissions_from_NG | LifeCycle_Emission_Reduction_Fraction | npv | lcc
Chicago | 388 | 513041 | 490374 | 0 | 1714 | 0 | 2077.939 | 10 | 13 | 3687.428 | 2554665 | 877.2916 | 877.2916 | 974.7684 | 21932.29 | 24369.21 | 0 | 0 | 0.1 | -101132.32 | 6066885.1
Chicago | 754 | 998657 | 954535 | 0 | 91344 | 0 | 29741.281 | 31 | 122 | 34150.076 | 2183538 | 779.8148 | 779.8148 | 974.7684 | 19495.37 | 24369.21 | 0 | 0 | 0.2 | -336370.57 | 6302123.35
Chicago | 1068 | 1414304 | 1351819 | 0 | 281393 | 0 | 122003.81 | 70 | 495 | 134090.409 | 1987469 | 682.338 | 682.338 | 974.7684 | 17058.45 | 24369.21 | 0 | 0 | 0.3 | -764792.53 | 6730545.31
Chicago | 1356 | 1795117 | 1715807 | 0 | 449974 | 0 | 254114.48 | 142 | 1014 | 269050.907 | 1807133 | 584.8612 | 584.8612 | 974.7684 | 14621.53 | 24369.21 | 0 | 0 | 0.4 | -1242357.5 | 7208110.28
Chicago | 1658 | 2194291 | 2097345 | 0 | 661268 | 0 | 375649.953 | 196 | 1487 | 387143.008 | 1650070 | 487.3844 | 487.3844 | 974.7684 | 12184.61 | 24369.21 | 0 | 0 | 0.5 | -1741898.23 | 7707651.02
Chicago | 1960 | 2594171 | 2479558 | 0 | 878667 | 0 | 500709.779 | 250 | 1970 | 504261.015 | 1498325 | 389.9072 | 389.9072 | 974.7684 | 9747.68 | 24369.21 | 0 | 0 | 0.6 | -2252717.14 | 8218469.92
Chicago | 2274 | 3010262 | 2877266 | 0 | 1128002 | 0 | 612353.665 | 294 | 2392 | 606327.854 | 1361342 | 292.4304 | 292.4304 | 974.7684 | 7310.76 | 24369.21 | 0 | 0 | 0.7 | -2771749.42 | 8737502.2
Chicago | 2581 | 3415949 | 3265029 | 0 | 1365079 | 0 | 735533.864 | 345 | 2855 | 718942.387 | 1223222 | 194.9536 | 194.9536 | 974.7684 | 4873.84 | 24369.21 | 0 | 0 | 0.8 | -3298381.3 | 9264134.09
Chicago | 2900 | 3838771 | 3669171 | 0 | 1634460 | 0 | 844780.461 | 391 | 3245 | 816071.382 | 1099304 | 97.4768 | 97.4768 | 974.7684 | 2436.92 | 24369.21 | 0 | 0 | 0.9 | -3831654.32 | 9797407.1
Chicago | 2900 | 3838771 | 3669171 | 0 | 1192888 | 0 | 1352662.97 | 682 | 5425 | 1363812.997 | 718877 | 0 | 0 | 974.7684 | 0 | 24369.21 | 0 | 0 | 1 | -4524826.16 | 10490578.94

## CermakA_3
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Grid_Electricity_Supplied_kWh_annual | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | NG_LifeCycle_Emissions_CO2 | Emissions_from_NG | LifeCycle_Emission_Reduction_Fraction | npv | lcc
Chicago | 2845 | 3766166 | 3599773 | 0 | 2349945 | 0 | 6270.593 | 14 | 18 | 5644.442 | 1793717 | 264.466 | 264.466 | 974.7684 | 6611.65 | 24369.21 | 0 | 0 | 0.73 | 1553992.05 | 4411760.73
Chicago | 2845 | 3766166 | 3599773 | 0 | 2349945 | 0 | 6270.593 | 14 | 18 | 5644.442 | 1793717 | 264.466 | 264.466 | 974.7684 | 6611.65 | 24369.21 | 0 | 0 | 0.73 | 1553992.05 | 4411760.73
Chicago | 2845 | 3766166 | 3599773 | 0 | 2349945 | 0 | 6270.593 | 14 | 18 | 5644.442 | 1793717 | 264.466 | 264.466 | 974.7684 | 6611.65 | 24369.21 | 0 | 0 | 0.73 | 1553992.05 | 4411760.73
Chicago | 2845 | 3766166 | 3599773 | 0 | 2349945 | 0 | 6270.593 | 14 | 18 | 5644.442 | 1793717 | 264.466 | 264.466 | 974.7684 | 6611.65 | 24369.21 | 0 | 0 | 0.73 | 1553992.05 | 4411760.73
Chicago | 2845 | 3766166 | 3599773 | 0 | 2349945 | 0 | 6270.593 | 14 | 18 | 5644.442 | 1793717 | 264.466 | 264.466 | 974.7684 | 6611.65 | 24369.21 | 0 | 0 | 0.73 | 1553992.05 | 4411760.73
Chicago | 2845 | 3766166 | 3599773 | 0 | 2349945 | 0 | 6270.593 | 14 | 18 | 5644.442 | 1793717 | 264.466 | 264.466 | 974.7684 | 6611.65 | 24369.21 | 0 | 0 | 0.73 | 1553992.05 | 4411760.73
Chicago | 2845 | 3766166 | 3599773 | 0 | 2349945 | 0 | 6270.593 | 14 | 18 | 5644.442 | 1793717 | 264.466 | 264.466 | 974.7684 | 6611.65 | 24369.21 | 0 | 0 | 0.73 | 1553992.05 | 4411760.73
Chicago | 2900 | 3838771 | 3669171 | 0 | 2349945 | 0 | 258798.269 | 132 | 1077 | 292487.221 | 1756367 | 194.9536 | 194.9536 | 974.7684 | 4873.84 | 24369.21 | 0 | 0 | 0.8 | 1211270.8 | 4754481.98
Chicago | 2900 | 3838771 | 3669171 | 0 | 2110935 | 0 | 648968.446 | 385 | 3075 | 799303.85 | 1573940 | 97.4768 | 97.4768 | 974.7684 | 2436.92 | 24369.21 | 0 | 0 | 0.9 | 379794.25 | 5585958.53
Chicago | 2900 | 3838771 | 3669171 | 0 | 1797039 | 0 | 1048909.678 | 654 | 5119 | 1349716.305 | 1321534 | 0 | 0 | 974.7684 | 0 | 24369.21 | 0 | 0 | 1 | -662933.19 | 6628685.97

## CermakA_4
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Grid_Electricity_Supplied_kWh_annual | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | NG_LifeCycle_Emissions_CO2 | Emissions_from_NG | LifeCycle_Emission_Reduction_Fraction | npv | lcc
Chicago | 2845 | 3766166 | 3599773 | 0 | 2349945 | 0 | 6270.593 | 14 | 18 | 5644.442 | 1793717 | 264.466 | 264.466 | 974.7684 | 6611.65 | 24369.21 | 0 | 0 | 73% | 1553992.05 | 4411760.73
Chicago | 2845 | 3766166 | 3599773 | 0 | 2349945 | 0 | 6270.593 | 14 | 18 | 5644.442 | 1793717 | 264.466 | 264.466 | 974.7684 | 6611.65 | 24369.21 | 0 | 0 | 73% | 1553992.05 | 4411760.73
Chicago | 2845 | 3766166 | 3599773 | 0 | 2349945 | 0 | 6270.593 | 14 | 18 | 5644.442 | 1793717 | 264.466 | 264.466 | 974.7684 | 6611.65 | 24369.21 | 0 | 0 | 73% | 1553992.05 | 4411760.73
Chicago | 2845 | 3766166 | 3599773 | 0 | 2349945 | 0 | 6270.593 | 14 | 18 | 5644.442 | 1793717 | 264.466 | 264.466 | 974.7684 | 6611.65 | 24369.21 | 0 | 0 | 73% | 1553992.05 | 4411760.73
Chicago | 2845 | 3766166 | 3599773 | 0 | 2349945 | 0 | 6270.593 | 14 | 18 | 5644.442 | 1793717 | 264.466 | 264.466 | 974.7684 | 6611.65 | 24369.21 | 0 | 0 | 73% | 1553992.05 | 4411760.73
Chicago | 2845 | 3766166 | 3599773 | 0 | 2349945 | 0 | 6270.593 | 14 | 18 | 5644.442 | 1793717 | 264.466 | 264.466 | 974.7684 | 6611.65 | 24369.21 | 0 | 0 | 73% | 1553992.05 | 4411760.73
Chicago | 2845 | 3766166 | 3599773 | 0 | 2349945 | 0 | 6270.593 | 14 | 18 | 5644.442 | 1793717 | 264.466 | 264.466 | 974.7684 | 6611.65 | 24369.21 | 0 | 0 | 73% | 1553992.05 | 4411760.73
Chicago | 2900 | 3838771 | 3669171 | 0 | 2349945 | 0 | 258798.269 | 132 | 1077 | 292487.221 | 1756367 | 194.9536 | 194.9536 | 974.7684 | 4873.84 | 24369.21 | 0 | 0 | 80% | 1211270.8 | 4754481.98
Chicago | 2900 | 3838771 | 3669171 | 0 | 2110935 | 0 | 648968.446 | 385 | 3075 | 799303.85 | 1573940 | 97.4768 | 97.4768 | 974.7684 | 2436.92 | 24369.21 | 0 | 0 | 90% | 379794.25 | 5585958.53
Chicago | 2900 | 3838771 | 3669171 | 0 | 1797039 | 0 | 1048909.678 | 654 | 5119 | 1349716.305 | 1321534 | 0 | 0 | 974.7684 | 0 | 24369.21 | 0 | 0 | 100% | -662933.19 | 6628685.97
This scenario has a wholesale rate this is equal to the retail rate.

## CermakB_0
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | ASHP_size_tonhour | ASHP_annual_electric_consumption_kwh | ASHP_annual_thermal_production_mmbtu | ASHP_annual_cooling_tonhour | Grid_Electricity_Supplied_kWh_annual | Annual_Total_HeatingLoad_MMBtu | BAU_Existing_Boiler_Fuel_Consump_MMBtu | BAU_Existing_Boiler_Thermal_Prod_MMBtu | NG_Annual_Consumption_MMBtu | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | NG_LifeCycle_Emissions_CO2 | Emissions_from_NG | LifeCycle_Emission_Reduction_Fraction | npv | lcc
Chicago | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chicago | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chicago | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chicago | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Chicago | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## CermakB_1
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | ASHP_size_tonhour | ASHP_annual_electric_consumption_kwh | ASHP_annual_thermal_production_mmbtu | ASHP_annual_cooling_tonhour | Grid_Electricity_Supplied_kWh_annual | Annual_Total_HeatingLoad_MMBtu | BAU_Existing_Boiler_Fuel_Consump_MMBtu | BAU_Existing_Boiler_Thermal_Prod_MMBtu | NG_Annual_Consumption_MMBtu | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | NG_LifeCycle_Emissions_CO2 | Emissions_from_NG | LifeCycle_Emission_Reduction_Fraction | npv | lcc
Chicago | 2405 | 3183584 | 3042930 | 0 | 1836382 | 0 | 134.217 | 10 | 13 | 189.089 | 0 | 0 | 0 | 0 | 1836382 | 22691 | 30255 | 22691 | 30255 | 1980.6248 | 374.5752 | 2580.818 | 49515.62 | 64520.45 | 40151.23 | 1606 | 23% | 1318306.19 | 7861753.04
Chicago | 2405 | 3183584 | 3042930 | 0 | 1836382 | 0 | 134.217 | 10 | 13 | 189.089 | 0 | 0 | 0 | 0 | 1836382 | 22691 | 30255 | 22691 | 30255 | 1980.6248 | 374.5752 | 2580.818 | 49515.62 | 64520.45 | 40151.23 | 1606 | 23% | 1318306.19 | 7861753.04
Chicago | 2900 | 3838771 | 3669171 | 0 | 2178912 | 0 | 267366.145 | 117 | 970 | 263729.679 | 0 | 0 | 0 | 0 | 1582121 | 22691 | 30255 | 22691 | 30255 | 1806.5724 | 200.5232 | 2580.818 | 45164.31 | 64520.45 | 40151.23 | 1606 | 30% | 610337.58 | 8569721.65
Chicago | 2900 | 3838771 | 3669171 | 0 | 1152094 | 0 | 1561644.053 | 953 | 6775 | 1806034.648 | 0 | 0 | 0 | 0 | 727580 | 22691 | 30255 | 22691 | 30255 | 1548.4908 | -57.5588 | 2580.818 | 38712.27 | 64520.45 | 40151.23 | 1606 | 40% | -2139855.15 | 11319914.38
Chicago | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0

## CermakA_5
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Grid_Electricity_Supplied_kWh_annual | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | NG_LifeCycle_Emissions_CO2 | Emissions_from_NG | LifeCycle_Emission_Reduction_Fraction | npv | lcc
Chicago | 388 | 513036 | 490370 | 0 | 1714 | 0 | 2200.428 | 10 | 13 | 3700.671 | 2554671 | 877.2916 | 877.2916 | 974.7684 | 21932.29 | 24369.21 | 0 | 0 | 0.1 | -170580.06 | 6136332.84
Chicago | 765 | 1012105 | 967389 | 0 | 105656 | 0 | 19181.776 | 27 | 75 | 21480.557 | 2183583 | 779.8148 | 779.8148 | 974.7684 | 19495.37 | 24369.21 | 0 | 0 | 0.2 | -428495.77 | 6394248.55
Chicago | 1169 | 1546990 | 1478643 | 0 | 471732 | 0 | 3625.341 | 10 | 14 | 3793.521 | 2036427 | 682.338 | 682.338 | 974.7684 | 17058.45 | 24369.21 | 0 | 0 | 0.3 | -565360.08 | 6531112.86
Chicago | 1559 | 2063963 | 1972775 | 0 | 877576 | 0 | 3770.945 | 10 | 14 | 3846.89 | 1948144 | 584.8612 | 584.8612 | 974.7684 | 14621.53 | 24369.21 | 0 | 0 | 0.4 | -766364.03 | 6732116.81
Chicago | 1950 | 2581211 | 2467171 | 0 | 1310363 | 0 | 3665.169 | 10 | 13 | 3659.575 | 1886515 | 487.3844 | 487.3844 | 974.7684 | 12184.61 | 24369.21 | 0 | 0 | 0.5 | -967545.04 | 6933297.82
Chicago | 2340 | 3098070 | 2961195 | 0 | 1757659 | 0 | 3911.642 | 10 | 14 | 3829.182 | 1839806 | 389.9072 | 389.9072 | 974.7684 | 9747.68 | 24369.21 | 0 | 0 | 0.6 | -1168835.2 | 7134587.98
Chicago | 2441 | 3231149 | 3088394 | 0 | 1539276 | 0 | 378451.15 | 183 | 1423 | 382211.562 | 1536494 | 292.4304 | 292.4304 | 974.7684 | 7310.76 | 24369.21 | 0 | 0 | 0.7 | -1733179.86 | 7698932.64
Chicago | 2792 | 3696456 | 3533143 | 0 | 1896242 | 0 | 437622.435 | 208 | 1614 | 433382.683 | 1454426 | 194.9536 | 194.9536 | 974.7684 | 4873.84 | 24369.21 | 0 | 0 | 0.8 | -2457692.72 | 8423445.5
Chicago | 2900 | 3838771 | 3669171 | 0 | 1686319 | 0 | 810425.254 | 384 | 3084 | 801340.093 | 1149551 | 97.4768 | 97.4768 | 974.7684 | 2436.92 | 24369.21 | 0 | 0 | 0.9 | -3236706.18 | 9202458.96
Chicago | 2900 | 3838771 | 3669171 | 0 | 1204574 | 0 | 1339709.443 | 708 | 5311 | 1355711.91 | 729685 | 0 | 0 | 974.7684 | 0 | 24369.21 | 0 | 0 | 1 | -4367591.8 | 10333344.58

## CermakA_6
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Grid_Electricity_Supplied_kWh_annual | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | LifeCycle_Emission_Reduction_Fraction | LifeCycle_capex_costs_for_generation_techs | LifeCycle_capex_costs_for_battery | Initial_upfront_capex_wo_incentives | Initial_upfront_capex_w_incentives | Yr1_energy_cost_after_tax | Yr1_demand_cost_after_tax | Yr1_total_energy_bill_before_tax | Yr1_export_benefit_before_tax | Annual_renewable_electricity_kwh | Annual_renewable_electricity_kwh_fraction | npv | lcc
Chicago | 25 | 33093 | 31631 | 0 | 0 | 0 | 2789.58 | 204 | 1532 | 40750.753 | 3015398 | 974.7676 | 974.7676 | 974.7684 | 24369.19 | 24369.21 | 0 | 42449.42 | 0 | 983597.42 | 462308.36 | 338026.17 | 43862.82 | 610681.99 | 0 | 31347.8 | 0.01 | -544848.07 | 6529404.04
Chicago | 669 | 884944 | 845846 | 0 | 23913 | 0 | 86082.755 | 181 | 1713 | 125530.327 | 2234609 | 787.0876 | 787.0876 | 974.7684 | 19677.19 | 24369.21 | 0.19 | 1135150.02 | 0 | 3642148.32 | 1593461.56 | 250499.72 | 39088.76 | 518381.48 | 2678 | 837114.04 | 0.28 | -870841.99 | 6877347.78
Chicago | 1158 | 1532530 | 1464821 | 0 | 290830 | 0 | 205444.057 | 256 | 2075 | 217953.836 | 1892870 | 646.7484 | 646.7484 | 974.7684 | 16168.71 | 24369.21 | 0.34 | 1965833.15 | 0 | 5850073.36 | 2529886.98 | 212190.73 | 35747.54 | 476731.27 | 32569 | 1443981.69 | 0.47 | -1244829.75 | 7270693.13

## CermakA_7
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Grid_Electricity_Supplied_kWh_annual | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | LifeCycle_Emission_Reduction_Fraction | LifeCycle_capex_costs_for_generation_techs | LifeCycle_capex_costs_for_battery | Initial_upfront_capex_wo_incentives | Initial_upfront_capex_w_incentives | Yr1_energy_cost_after_tax | Yr1_demand_cost_after_tax | Yr1_total_energy_bill_before_tax | Yr1_export_benefit_before_tax | Annual_renewable_electricity_kwh | Annual_renewable_electricity_kwh_fraction | npv | lcc
Chicago | 25 | 33093 | 31631 | 0 | 0 | 0 | 2789.58 | 204 | 1532 | 40750.753 | 3015398 | 974.7676 | 974.7676 | 974.7684 | 24369.19 | 24369.21 | 0 | 42449.42 | 0 | 983597.42 | 462308.36 | 338026.17 | 43862.82 | 610681.99 | 0 | 31347.8 | 0.01 | -544848.07 | 6529404.04
Chicago | 669 | 884944 | 845846 | 0 | 23913 | 0 | 86082.755 | 181 | 1713 | 125530.327 | 2234609 | 787.0876 | 787.0876 | 974.7684 | 19677.19 | 24369.21 | 0.19 | 1135150.02 | 0 | 3642148.32 | 1593461.56 | 250499.72 | 39088.76 | 518381.48 | 2678 | 837114.04 | 0.28 | -870841.99 | 6877347.78
Chicago | 1158 | 1532530 | 1464821 | 0 | 290830 | 0 | 205444.057 | 256 | 2075 | 217953.836 | 1892870 | 646.7484 | 646.7484 | 974.7684 | 16168.71 | 24369.21 | 0.34 | 1965833.15 | 0 | 5850073.36 | 2529886.98 | 212190.73 | 35747.54 | 476731.27 | 32569 | 1443981.69 | 0.47 | -1244829.75 | 7270693.13

## CermakA_8
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Grid_Electricity_Supplied_kWh_annual | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | LifeCycle_Emission_Reduction_Fraction | LifeCycle_capex_costs_for_generation_techs | LifeCycle_capex_costs_for_battery | Initial_upfront_capex_wo_incentives | Initial_upfront_capex_w_incentives | Yr1_energy_cost_after_tax | Yr1_demand_cost_after_tax | Yr1_total_energy_bill_before_tax | Yr1_export_benefit_before_tax | Annual_renewable_electricity_kwh | Annual_renewable_electricity_kwh_fraction | npv | lcc
Chicago | 25 | 33093 | 31631 | 0 | 0 | 0 | 2789.58 | 204 | 1532 | 40750.753 | 3015398 | 974.7676 | 974.7676 | 974.7684 | 24369.19 | 24369.21 | 0 | 42449.42 | 0 | 983597.42 | 462308.36 | 338026.17 | 43862.82 | 610681.99 | 0 | 31347.8 | 0.01 | -544848.07 | 6529404.04
Chicago | 669 | 884944 | 845846 | 0 | 23913 | 0 | 86082.755 | 181 | 1713 | 125530.327 | 2234609 | 787.0876 | 787.0876 | 974.7684 | 19677.19 | 24369.21 | 0.19 | 1135150.02 | 0 | 3642148.32 | 1593461.56 | 250499.72 | 39088.76 | 518381.48 | 2678 | 837114.04 | 0.28 | -870841.99 | 6877347.78
Chicago | 1158 | 1532530 | 1464821 | 0 | 290830 | 0 | 205444.057 | 256 | 2075 | 217953.836 | 1892870 | 646.7484 | 646.7484 | 974.7684 | 16168.71 | 24369.21 | 0.34 | 1965833.15 | 0 | 5850073.36 | 2529886.98 | 212190.73 | 35747.54 | 476731.27 | 32569 | 1443981.69 | 0.47 | -1244829.75 | 7270693.13

## CermakA_9
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Grid_Electricity_Supplied_kWh_annual | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | LifeCycle_Emission_Reduction_Fraction | LifeCycle_capex_costs_for_generation_techs | LifeCycle_capex_costs_for_battery | Initial_upfront_capex_wo_incentives | Initial_upfront_capex_w_incentives | Yr1_energy_cost_after_tax | Yr1_demand_cost_after_tax | Yr1_total_energy_bill_before_tax | Yr1_export_benefit_before_tax | Annual_renewable_electricity_kwh | Annual_renewable_electricity_kwh_fraction | npv | lcc
Chicago | 25 | 33093 | 31631 | 0 | 0 | 0 | 2789.58 | 204 | 1532 | 40750.753 | 3015398 | 974.7676 | 974.7676 | 974.7684 | 24369.19 | 24369.21 | 0% | 42449.42 | 0 | 983597.42 | 462308.36 | 338026.17 | 43862.82 | 610681.99 | 0 | 31347.8 | 1% | -544848.07 | 6529404.04
Chicago | 669 | 884944 | 845846 | 0 | 23913 | 0 | 86082.755 | 181 | 1713 | 125530.327 | 2234609 | 787.0876 | 787.0876 | 974.7684 | 19677.19 | 24369.21 | 19% | 1135150.02 | 0 | 3642148.32 | 1593461.56 | 250499.72 | 39088.76 | 518381.48 | 2678 | 837114.04 | 28% | -870841.99 | 6877347.78
Chicago | 1158 | 1532530 | 1464821 | 0 | 290830 | 0 | 205444.057 | 256 | 2075 | 217953.836 | 1892870 | 646.7484 | 646.7484 | 974.7684 | 16168.71 | 24369.21 | 34% | 1965833.15 | 0 | 5850073.36 | 2529886.98 | 212190.73 | 35747.54 | 476731.27 | 32569 | 1443981.69 | 47% | -1244829.75 | 7270693.13
outage durations = 8, 16, 24 hour durations

## MarkhamA_0
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Grid_Electricity_Supplied_kWh_annual | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | LifeCycle_Emission_Reduction_Fraction | LifeCycle_capex_costs_for_generation_techs | LifeCycle_capex_costs_for_battery | Initial_upfront_capex_wo_incentives | Initial_upfront_capex_w_incentives | Yr1_energy_cost_after_tax | Yr1_demand_cost_after_tax | Yr1_total_energy_bill_before_tax | Yr1_export_benefit_before_tax | Annual_renewable_electricity_kwh | Annual_renewable_electricity_kwh_fraction | npv | lcc
Chicago | 1036 | 1371495 | 1310901 | 0 | 0 | 0 | 125642.653 | 377 | 1854 | 285660.782 | 3280567 | 960.1912 | 960.1912 | 1066.8792 | 24004.78 | 26671.98 | 10% | 497669.94 | 0 | 2369556.48 | 1036462.67 | 382186 | 92100.38 | 493469.38 | 0 | 1298155.6 | 28% | -672770.65 | 6233671.2
Chicago | 1357 | 1796899 | 1717510 | 0 | 2957 | 0 | 238770.416 | 403 | 2074 | 411767.919 | 2891081 | 853.5036 | 853.5036 | 1066.8792 | 21337.59 | 26671.98 | 20% | 1043351.3 | 0 | 3790293.6 | 1641566.93 | 336810.95 | 85034.2 | 441028.15 | 166 | 1693289.22 | 37% | -819362.37 | 6420739.98
Chicago | 1443 | 1910119 | 1825728 | 0 | 10426 | 0 | 441540.079 | 402 | 3039 | 793468.104 | 2833117 | 746.8156 | 746.8156 | 1066.8792 | 18670.39 | 26671.98 | 30% | 1188583.62 | 0 | 4573690.64 | 2020809.06 | 330058.19 | 116801.73 | 466042.92 | 584 | 1780938.75 | 39% | -1532406.24 | 7152790.26
outage durations = 8, 16, 24 hour durations

## ProvdientA_0
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Grid_Electricity_Supplied_kWh_annual | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | LifeCycle_Emission_Reduction_Fraction | LifeCycle_capex_costs_for_generation_techs | LifeCycle_capex_costs_for_battery | Initial_upfront_capex_wo_incentives | Initial_upfront_capex_w_incentives | Yr1_energy_cost_after_tax | Yr1_demand_cost_after_tax | Yr1_total_energy_bill_before_tax | Yr1_export_benefit_before_tax | Annual_renewable_electricity_kwh | Annual_renewable_electricity_kwh_fraction | npv | lcc
Chicago | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 808 | 6611 | 122051.651 | 11383397 | 3660.2364 | 3660.2364 | 3641.0904 | 91505.91 | 91027.26 | -1% | 0 | 0 | 3743285.08 | 1794788.42 | 1326165.78 | 194430.09 | 1539778.87 | 0 | 0 | 0% | -2340413.28 | 17442687.25
Chicago | 337 | 445833 | 426136 | 0 | 0 | 0 | 47555.788 | 795 | 12633 | 167697.893 | 10960508 | 3555.054 | 3555.054 | 3641.0904 | 88876.35 | 91027.26 | 2% | 571886.56 | 0 | 7830703.33 | 3825324.35 | 1276899.24 | 182310.51 | 1478392.75 | 0 | 421311.79 | 4% | -4389199.67 | 19579566.42
Chicago | 337 | 445833 | 426136 | 0 | 0 | 0 | 57349.862 | 813 | 18927 | 220380.504 | 10964464 | 3553.5628 | 3553.5628 | 3641.0904 | 88839.07 | 91027.26 | 2% | 571886.56 | 0 | 10710456.77 | 5357074.07 | 1277360.07 | 179370.75 | 1475913.82 | 0 | 420318.28 | 4% | -6484671.67 | 21759024.4
outage durations = 8, 16, 24 hour durations

## CermakA_10
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Grid_Electricity_Supplied_kWh_annual | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | LifeCycle_Emission_Reduction_Fraction | LifeCycle_capex_costs_for_generation_techs | LifeCycle_capex_costs_for_battery | Initial_upfront_capex_wo_incentives | Initial_upfront_capex_w_incentives | Yr1_energy_cost_after_tax | Yr1_demand_cost_after_tax | Yr1_total_energy_bill_before_tax | Yr1_export_benefit_before_tax | Annual_renewable_electricity_kwh | Annual_renewable_electricity_kwh_fraction | npv | lcc
Chicago | 25 | 33093 | 31631 | 0 | 0 | 0 | 2789.58 | 204 | 1532 | 40750.753 | 3015398 | 974.7676 | 974.7676 | 974.7684 | 24369.19 | 24369.21 | 0 | 42449.42 | 0 | 983597.42 | 462308.36 | 338026.17 | 43862.82 | 610681.99 | 0 | 31347.8 | 0.01 | -544848.07 | 6529404.04
Chicago | 669 | 884944 | 845846 | 0 | 23913 | 0 | 86082.755 | 181 | 1713 | 125530.327 | 2234609 | 787.0876 | 787.0876 | 974.7684 | 19677.19 | 24369.21 | 0.19 | 1135150.02 | 0 | 3642148.32 | 1593461.56 | 250499.72 | 39088.76 | 518381.48 | 2678 | 837114.04 | 0.28 | -870841.99 | 6877347.78
Chicago | 1158 | 1532530 | 1464821 | 0 | 290830 | 0 | 205444.057 | 256 | 2075 | 217953.836 | 1892870 | 646.7484 | 646.7484 | 974.7684 | 16168.71 | 24369.21 | 0.34 | 1965833.15 | 0 | 5850073.36 | 2529886.98 | 212190.73 | 35747.54 | 476731.27 | 32569 | 1443981.69 | 0.47 | -1244829.75 | 7270693.13

## CermakA_11
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Grid_Electricity_Supplied_kWh_annual | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | LifeCycle_Emission_Reduction_Fraction | LifeCycle_capex_costs_for_generation_techs | LifeCycle_capex_costs_for_battery | Initial_upfront_capex_wo_incentives | Initial_upfront_capex_w_incentives | Yr1_energy_cost_after_tax | Yr1_demand_cost_after_tax | Yr1_total_energy_bill_before_tax | Yr1_export_benefit_before_tax | Annual_renewable_electricity_kwh | Annual_renewable_electricity_kwh_fraction | npv | lcc
Chicago | 25 | 33093 | 31631 | 0 | 0 | 0 | 2789.58 | 204 | 1532 | 40750.753 | 3015398 | 974.7676 | 974.7676 | 974.7684 | 24369.19 | 24369.21 | 0 | 42449.42 | 0 | 983597.42 | 462308.36 | 338026.17 | 43862.82 | 610681.99 | 0 | 31347.8 | 0.01 | -544848.07 | 6529404.04
Chicago | 669 | 884944 | 845846 | 0 | 23913 | 0 | 86082.755 | 181 | 1713 | 125530.327 | 2234609 | 787.0876 | 787.0876 | 974.7684 | 19677.19 | 24369.21 | 0.19 | 1135150.02 | 0 | 3642148.32 | 1593461.56 | 250499.72 | 39088.76 | 518381.48 | 2678 | 837114.04 | 0.28 | -870841.99 | 6877347.78
Chicago | 1158 | 1532530 | 1464821 | 0 | 290830 | 0 | 205444.057 | 256 | 2075 | 217953.836 | 1892870 | 646.7484 | 646.7484 | 974.7684 | 16168.71 | 24369.21 | 0.34 | 1965833.15 | 0 | 5850073.36 | 2529886.98 | 212190.73 | 35747.54 | 476731.27 | 32569 | 1443981.69 | 0.47 | -1244829.75 | 7270693.13

## MarkhamA_1
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Grid_Electricity_Supplied_kWh_annual | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | LifeCycle_Emission_Reduction_Fraction | LifeCycle_capex_costs_for_generation_techs | LifeCycle_capex_costs_for_battery | Initial_upfront_capex_wo_incentives | Initial_upfront_capex_w_incentives | Yr1_energy_cost_after_tax | Yr1_demand_cost_after_tax | Yr1_total_energy_bill_before_tax | Yr1_export_benefit_before_tax | Annual_renewable_electricity_kwh | Annual_renewable_electricity_kwh_fraction | npv | lcc
Chicago | 1036 | 1371495 | 1310901 | 0 | 0 | 0 | 126652.283 | 377 | 1854 | 285660.782 | 3280567 | 960.1912 | 960.1912 | 1066.8792 | 24004.78 | 26671.98 | 0.1 | 497669.94 | 0 | 2369556.48 | 1036462.67 | 382186 | 92100.38 | 493469.38 | 0 | 1298053.18 | 0.28 | -672770.65 | 6233671.2
Chicago | 1357 | 1796899 | 1717510 | 0 | 2957 | 0 | 239700.482 | 403 | 2074 | 411767.919 | 2891081 | 853.5036 | 853.5036 | 1066.8792 | 21337.59 | 26671.98 | 0.2 | 1043351.3 | 0 | 3790293.6 | 1641566.93 | 336810.95 | 85034.2 | 441028.15 | 166 | 1693194.87 | 0.37 | -819362.37 | 6420739.98
Chicago | 1804 | 2387870 | 2282372 | 0 | 96018 | 0 | 254125.166 | 398 | 2246 | 348767.327 | 2412114 | 746.8156 | 746.8156 | 1066.8792 | 18670.39 | 26671.98 | 0.3 | 1801411.96 | 0 | 5665663.84 | 2440192.12 | 281011.25 | 79378.81 | 379573.06 | 5377 | 2256593.33 | 0.49 | -1055703.9 | 6676087.92

## CermakA_12
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Grid_Electricity_Supplied_kWh_annual | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | LifeCycle_Emission_Reduction_Fraction | LifeCycle_capex_costs_for_generation_techs | LifeCycle_capex_costs_for_battery | Initial_upfront_capex_wo_incentives | Initial_upfront_capex_w_incentives | Yr1_energy_cost_after_tax | Yr1_demand_cost_after_tax | Yr1_total_energy_bill_before_tax | Yr1_export_benefit_before_tax | Annual_renewable_electricity_kwh | Annual_renewable_electricity_kwh_fraction | npv | lcc
Chicago | 25 | 33093 | 31631 | 0 | 0 | 0 | 2892.452 | 204 | 1532 | 40750.753 | 3015398 | 974.7676 | 974.7676 | 974.7684 | 24369.19 | 24369.21 | 0% | 42449.42 | 0 | 983597.42 | 462308.36 | 338026.17 | 43862.82 | 610681.99 | 0 | 31337.37 | 1% | -544848.07 | 6529404.04
Chicago | 175 | 231650 | 221416 | 0 | 0 | 0 | 35368.813 | 186 | 2630 | 79483.808 | 2829639 | 923.6536 | 923.6536 | 974.7684 | 23091.34 | 24369.21 | 5% | 297145.91 | 0 | 2072513.31 | 979362.5 | 317202.52 | 40979.95 | 586975.47 | 0 | 217827.64 | 7% | -951378.55 | 6957884.34
Chicago | 175 | 231650 | 221416 | 0 | 0 | 0 | 35568.173 | 188 | 4005 | 86324.999 | 2829976 | 923.7276 | 923.7276 | 974.7684 | 23093.19 | 24369.21 | 5% | 297145.91 | 0 | 2699344.77 | 1313386.47 | 317240.32 | 40824.83 | 586858.15 | 0 | 217807.42 | 7% | -1411012.54 | 7436875.91

## CermakA_13
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Grid_Electricity_Supplied_kWh_annual | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | LifeCycle_Emission_Reduction_Fraction | LifeCycle_capex_costs_for_generation_techs | LifeCycle_capex_costs_for_battery | Initial_upfront_capex_wo_incentives | Initial_upfront_capex_w_incentives | Yr1_energy_cost_after_tax | Yr1_demand_cost_after_tax | Yr1_total_energy_bill_before_tax | Yr1_export_benefit_before_tax | Annual_renewable_electricity_kwh | Annual_renewable_electricity_kwh_fraction | npv | lcc
Chicago | 25 | 33093 | 31631 | 0 | 0 | 0 | 2892.452 | 204 | 1532 | 40750.753 | 3015398 | 974.7676 | 974.7676 | 974.7684 | 24369.19 | 24369.21 | 0 | 42449.42 | 0 | 983597.42 | 462308.36 | 338026.17 | 43862.82 | 610681.99 | 0 | 31337.37 | 0.01 | -544848.07 | 6529404.04
Chicago | 175 | 231650 | 221416 | 0 | 0 | 0 | 35368.813 | 186 | 2630 | 79483.808 | 2829639 | 923.6536 | 923.6536 | 974.7684 | 23091.34 | 24369.21 | 0.05 | 297145.91 | 0 | 2072513.31 | 979362.5 | 317202.52 | 40979.95 | 586975.47 | 0 | 217827.64 | 0.07 | -951378.55 | 6957884.34
Chicago | 175 | 231650 | 221416 | 0 | 0 | 0 | 35568.173 | 188 | 4005 | 86324.999 | 2829976 | 923.7276 | 923.7276 | 974.7684 | 23093.19 | 24369.21 | 0.05 | 297145.91 | 0 | 2699344.77 | 1313386.47 | 317240.32 | 40824.83 | 586858.15 | 0 | 217807.42 | 0.07 | -1411012.54 | 7436875.91

## CermakA_14
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Grid_Electricity_Supplied_kWh_annual | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | LifeCycle_Emission_Reduction_Fraction | LifeCycle_capex_costs_for_generation_techs | LifeCycle_capex_costs_for_battery | Initial_upfront_capex_wo_incentives | Initial_upfront_capex_w_incentives | Yr1_energy_cost_after_tax | Yr1_demand_cost_after_tax | Yr1_total_energy_bill_before_tax | Yr1_export_benefit_before_tax | Annual_renewable_electricity_kwh | Annual_renewable_electricity_kwh_fraction | npv | lcc
Chicago | 25 | 33093 | 31631 | 0 | 0 | 0 | 2892.452 | 204 | 1532 | 40750.753 | 3015398 | 974.7676 | 974.7676 | 974.7684 | 24369.19 | 24369.21 | 0 | 42449.42 | 0 | 983597.42 | 462308.36 | 338026.17 | 43862.82 | 610681.99 | 0 | 31337.37 | 0.01 | -544848.07 | 6529404.04
Chicago | 175 | 231650 | 221416 | 0 | 0 | 0 | 35368.813 | 186 | 2630 | 79483.808 | 2829639 | 923.6536 | 923.6536 | 974.7684 | 23091.34 | 24369.21 | 0.05 | 297145.91 | 0 | 2072513.31 | 979362.5 | 317202.52 | 40979.95 | 586975.47 | 0 | 217827.64 | 0.07 | -951378.55 | 6957884.34
Chicago | 175 | 231650 | 221416 | 0 | 0 | 0 | 35568.173 | 188 | 4005 | 86324.999 | 2829976 | 923.7276 | 923.7276 | 974.7684 | 23093.19 | 24369.21 | 0.05 | 297145.91 | 0 | 2699344.77 | 1313386.47 | 317240.32 | 40824.83 | 586858.15 | 0 | 217807.42 | 0.07 | -1411012.54 | 7436875.91

## CermakA_15
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Grid_Electricity_Supplied_kWh_annual | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | LifeCycle_Emission_Reduction_Fraction | LifeCycle_capex_costs_for_generation_techs | LifeCycle_capex_costs_for_battery | Initial_upfront_capex_wo_incentives | Initial_upfront_capex_w_incentives | Yr1_energy_cost_after_tax | Yr1_demand_cost_after_tax | Yr1_total_energy_bill_before_tax | Yr1_export_benefit_before_tax | Annual_renewable_electricity_kwh | Annual_renewable_electricity_kwh_fraction | npv | lcc
Chicago | 25 | 33093 | 31631 | 0 | 0 | 0 | 227.185 | 19 | 31 | 503.09 | 3011330 | 968.5348 | 968.5348 | 974.7684 | 24213.37 | 24369.21 | 1% | 160073.42 | 0 | 249405.08 | 171877.89 | 337570.09 | 50286.34 | 616649.43 | 0 | 31607.73 | 0.01 | -144035.66 | 6128591.62
Chicago | 39 | 52158 | 49854 | 0 | 0 | 0 | 172.763 | 12 | 24 | 314.806 | 2993088 | 964.9368 | 964.9368 | 974.7684 | 24123.42 | 24369.21 | 1% | 190890.6 | 0 | 304624.52 | 199434.86 | 335525.13 | 50250.12 | 614568.25 | 0 | 49836.5 | 0.02 | -132257.9 | 6138763.69
Chicago | 39 | 52158 | 49854 | 0 | 0 | 0 | 149.191 | 12 | 24 | 314.806 | 2993088 | 964.9368 | 964.9368 | 974.7684 | 24123.42 | 24369.21 | 1% | 190890.6 | 0 | 304624.52 | 199434.86 | 335525.13 | 50250.12 | 614568.25 | 0 | 49838.89 | 0.02 | -113332.79 | 6139196.16

## CermakA_16
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Generator_size | Generator_annual_fuel_consumption | Generator_annual_energy_produced | Grid_Electricity_Supplied_kWh_annual | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | LifeCycle_Emission_Reduction_Fraction | LifeCycle_capex_costs_for_generation_techs | LifeCycle_capex_costs_for_battery | Initial_upfront_capex_wo_incentives | Initial_upfront_capex_w_incentives | Yr1_energy_cost_after_tax | Yr1_demand_cost_after_tax | Yr1_total_energy_bill_before_tax | Yr1_export_benefit_before_tax | Annual_renewable_electricity_kwh | Annual_renewable_electricity_kwh_fraction | npv | lcc
Chicago | 25 | 33093 | 31631 | 0 | 0 | 0 | 227.185 | 19 | 31 | 503.09 | 180.96 | 0 | 0 | 3011330 | 968.5348 | 968.5348 | 974.7684 | 24213.37 | 24369.21 | 0.01 | 160073.42 | 0 | 249405.08 | 171877.89 | 337570.09 | 50286.34 | 616649.43 | 0 | 31607.73 | 0.01 | -144035.66 | 6128591.62
Chicago | 39 | 52158 | 49854 | 0 | 0 | 0 | 172.763 | 12 | 24 | 314.806 | 190.75 | 0 | 0 | 2993088 | 964.9368 | 964.9368 | 974.7684 | 24123.42 | 24369.21 | 0.01 | 190890.6 | 0 | 304624.52 | 199434.86 | 335525.13 | 50250.12 | 614568.25 | 0 | 49836.5 | 0.02 | -132257.9 | 6138763.69
Chicago | 39 | 52158 | 49854 | 0 | 0 | 0 | 149.191 | 12 | 24 | 314.806 | 190.75 | 0 | 0 | 2993088 | 964.9368 | 964.9368 | 974.7684 | 24123.42 | 24369.21 | 0.01 | 190890.6 | 0 | 304624.52 | 199434.86 | 335525.13 | 50250.12 | 614568.25 | 0 | 49838.89 | 0.02 | -113332.79 | 6139196.16

## MarkhamA_2
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Grid_Electricity_Supplied_kWh_annual | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | LifeCycle_Emission_Reduction_Fraction | LifeCycle_capex_costs_for_generation_techs | LifeCycle_capex_costs_for_battery | Initial_upfront_capex_wo_incentives | Initial_upfront_capex_w_incentives | Yr1_energy_cost_after_tax | Yr1_demand_cost_after_tax | Yr1_total_energy_bill_before_tax | Yr1_export_benefit_before_tax | Annual_renewable_electricity_kwh | Annual_renewable_electricity_kwh_fraction | npv | lcc
Chicago | 1486 | 1967039 | 1880133 | 0 | 28685 | 0 | 117347.667 | 355 | 1854 | 141040.445 | 2723692 | 872.5116 | 872.5116 | 1066.8792 | 21812.79 | 26671.98 | 18% | 1587289.92 | 0 | 4165840.93 | 2121030.17 | 317310.15 | 85438.33 | 421931.48 | 1606 | 1868229.76 | 41% | -1130499.54 | 6691400.09
Chicago | 1486 | 1967039 | 1880133 | 0 | 21745 | 0 | 163773.075 | 401 | 2058 | 216851.55 | 2725246 | 853.5036 | 853.5036 | 1066.8792 | 21337.59 | 26671.98 | 20% | 1587289.92 | 0 | 4300447.2 | 2181306.19 | 317491.18 | 83715.95 | 420390.13 | 1218 | 1863520.37 | 41% | -1171831.48 | 6773209.09
Chicago | 1486 | 1967039 | 1880133 | 0 | 11096 | 0 | 438864.694 | 401 | 2864 | 727260.51 | 2771963 | 746.8156 | 746.8156 | 1066.8792 | 18670.39 | 26671.98 | 30% | 1587289.92 | 0 | 4667216.17 | 2376958.18 | 322933.73 | 108688.12 | 450804.85 | 621 | 1835615.06 | 40% | -1731088.5 | 7351472.52

## ProvidentA_10
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Grid_Electricity_Supplied_kWh_annual | Generator_size_kw | Generator_annual_fuel_consumption | Generator_annual_energy_produced | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | LifeCycle_Emission_Reduction_Fraction | LifeCycle_capex_costs_for_generation_techs | LifeCycle_capex_costs_for_battery | Initial_upfront_capex_wo_incentives | Initial_upfront_capex_w_incentives | Yr1_energy_cost_after_tax | Yr1_demand_cost_after_tax | Yr1_total_energy_bill_before_tax | Yr1_export_benefit_before_tax | Annual_renewable_electricity_kwh | Annual_renewable_electricity_kwh_fraction | npv | lcc
Chicago | 38 | 50639 | 48402 | 0 | 0 | 0 | 65.358 | 10 | 13 | 154.426 | 11323322 | 808.23 | 0 | 0 | 3631.5468 | 3631.5468 | 3641.0904 | 90788.67 | 91027.26 | 0 | 590306.34 | 0 | 694245.1 | 595639.43 | 1319167.04 | 220602.28 | 1558952.32 | 0 | 48395.35 | 0 | -601719.55 | 15703993.52
Chicago | 38 | 50639 | 48402 | 0 | 0 | 0 | 75.307 | 10 | 13 | 154.426 | 11323322 | 868.65 | 0 | 0 | 3631.5468 | 3631.5468 | 3641.0904 | 90788.67 | 91027.26 | 0 | 629582.59 | 0 | 733521.35 | 634915.68 | 1319167.04 | 220602.28 | 1558952.32 | 0 | 48394.34 | 0 | -566729.71 | 15757096.46
Chicago | 38 | 50639 | 48402 | 0 | 0 | 0 | 70.024 | 10 | 13 | 154.426 | 11323322 | 868.66 | 0 | 0 | 3631.5468 | 3631.5468 | 3641.0904 | 90788.67 | 91027.26 | 0 | 629582.59 | 0 | 733521.35 | 634915.68 | 1319167.04 | 220602.28 | 1558952.32 | 0 | 48394.87 | 0 | -484663.97 | 15759016.71

## CermakA_17
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Battery_initial_capex_cost | Generator_size | Generator_annual_fuel_consumption | Generator_annual_energy_produced | Grid_Electricity_Supplied_kWh_annual | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | LifeCycle_Emission_Reduction_Fraction | LifeCycle_capex_costs_for_generation_techs | LifeCycle_capex_costs_for_battery | Initial_upfront_capex_wo_incentives | Initial_upfront_capex_w_incentives | Yr1_energy_cost_after_tax | Yr1_demand_cost_after_tax | Yr1_total_energy_bill_before_tax | Yr1_export_benefit_before_tax | Annual_renewable_electricity_kwh | Annual_renewable_electricity_kwh_fraction | npv | lcc
Chicago | 25 | 33093 | 31631 | 0 | 0 | 0 | 227.185 | 19 | 31 | 503.09 | 30885 | 181 | 0 | 0 | 3011330 | 968.5348 | 968.5348 | 974.7684 | 24213.37 | 24369.21 | 0.01 | 160073.42 | 19491.75 | 249405.08 | 171877.89 | 337570.09 | 50286.34 | 616649.43 | 0 | 31607.73 | 0.01 | -144035.66 | 6128591.62
Chicago | 39 | 52158 | 49854 | 0 | 0 | 0 | 172.763 | 12 | 24 | 314.806 | 21608 | 191 | 0 | 0 | 2993088 | 964.9368 | 964.9368 | 974.7684 | 24123.42 | 24369.21 | 0.01 | 190890.6 | 13893.38 | 304624.52 | 199434.86 | 335525.13 | 50250.12 | 614568.25 | 0 | 49836.5 | 0.02 | -132257.9 | 6138763.69
Chicago | 39 | 52158 | 49854 | 0 | 0 | 0 | 149.191 | 12 | 24 | 314.806 | 21608 | 191 | 0 | 0 | 2993088 | 964.9368 | 964.9368 | 974.7684 | 24123.42 | 24369.21 | 0.01 | 190890.6 | 13893.38 | 304624.52 | 199434.86 | 335525.13 | 50250.12 | 614568.25 | 0 | 49838.89 | 0.02 | -113332.79 | 6139196.16

## MarkhamA_3
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Battery_initial_capex_cost | Grid_Electricity_Supplied_kWh_annual | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | LifeCycle_Emission_Reduction_Fraction | LifeCycle_capex_costs_for_generation_techs | LifeCycle_capex_costs_for_battery | Initial_upfront_capex_wo_incentives | Initial_upfront_capex_w_incentives | Yr1_energy_cost_after_tax | Yr1_demand_cost_after_tax | Yr1_total_energy_bill_before_tax | Yr1_export_benefit_before_tax | Annual_renewable_electricity_kwh | Annual_renewable_electricity_kwh_fraction | npv | lcc
Chicago | 1486 | 1967039 | 1880133 | 0 | 28685 | 0 | 118704.246 | 355 | 1854 | 141040.445 | 1167093.2 | 2723692 | 872.5116 | 872.5116 | 1066.8792 | 21812.79 | 26671.98 | 0.18 | 1587289.92 | 815036.81 | 4165840.93 | 2121030.17 | 317310.15 | 85438.33 | 421931.48 | 1606 | 1868092.15 | 0.41 | -1130499.54 | 6691400.09
Chicago | 1486 | 1967039 | 1880133 | 0 | 21752 | 0 | 125566.465 | 401 | 2058 | 155115.643 | 1301700.4 | 2718284 | 872.8988 | 872.8988 | 1066.8792 | 21822.47 | 26671.98 | 0.18 | 1587289.92 | 907891.21 | 4300447.2 | 2181306.19 | 316680.05 | 83715.95 | 419579 | 1218 | 1867396.05 | 0.41 | -1164055.39 | 6765433
Chicago | 1486 | 1967039 | 1880133 | 0 | 5795 | 0 | 143010.325 | 401 | 2864 | 211486.659 | 1668471.35 | 2708436 | 878.5452 | 878.5452 | 1066.8792 | 21963.63 | 26671.98 | 0.18 | 1587289.92 | 1189001.73 | 4667216.17 | 2376958.18 | 315532.8 | 77275.38 | 411991.18 | 325 | 1865626.54 | 0.41 | -1362013.89 | 6982397.92
1486

## ProvidentA_11
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Battery_initial_capex_cost | Grid_Electricity_Supplied_kWh_annual | Generator_size | Generator_annual_fuel_consumption | Generator_annual_energy_produced | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | LifeCycle_Emission_Reduction_Fraction | LifeCycle_capex_costs_for_generation_techs | LifeCycle_capex_costs_for_battery | Initial_upfront_capex_wo_incentives | Initial_upfront_capex_w_incentives | Yr1_energy_cost_after_tax | Yr1_demand_cost_after_tax | Yr1_total_energy_bill_before_tax | Yr1_export_benefit_before_tax | Annual_renewable_electricity_kwh | Annual_renewable_electricity_kwh_fraction | npv | lcc
Chicago | 38 | 50639 | 48402 | 0 | 0 | 0 | 65.358 | 10 | 13 | 154.426 | 14496 | 11323322 | 808 | 0 | 0 | 3631.5468 | 3631.5468 | 3641.0904 | 90788.67 | 91027.26 | 0 | 590306.34 | 8963.71 | 694245.1 | 595639.43 | 1319167.04 | 220602.28 | 1558952.32 | 0 | 48395.35 | 0 | -601719.55 | 15703993.52
Chicago | 38 | 50639 | 48402 | 0 | 0 | 0 | 75.307 | 10 | 13 | 154.426 | 14496 | 11323322 | 869 | 0 | 0 | 3631.5468 | 3631.5468 | 3641.0904 | 90788.67 | 91027.26 | 0 | 629582.59 | 8963.71 | 733521.35 | 634915.68 | 1319167.04 | 220602.28 | 1558952.32 | 0 | 48394.34 | 0 | -566729.71 | 15757096.46
Chicago | 38 | 50639 | 48402 | 0 | 0 | 0 | 70.024 | 10 | 13 | 154.426 | 14496 | 11323322 | 869 | 0 | 0 | 3631.5468 | 3631.5468 | 3641.0904 | 90788.67 | 91027.26 | 0 | 629582.59 | 8963.71 | 733521.35 | 634915.68 | 1319167.04 | 220602.28 | 1558952.32 | 0 | 48394.87 | 0 | -484663.97 | 15759016.71

## CermakA_18
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Battery_initial_capex_cost | Generator_size | Generator_annual_fuel_consumption | Generator_annual_energy_produced | Grid_Electricity_Supplied_kWh_annual | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | LifeCycle_Emission_Reduction_Fraction | LifeCycle_capex_costs_for_generation_techs | LifeCycle_capex_costs_for_battery | Initial_upfront_capex_wo_incentives | Initial_upfront_capex_w_incentives | Yr1_energy_cost_after_tax | Yr1_demand_cost_after_tax | Yr1_total_energy_bill_before_tax | Yr1_export_benefit_before_tax | Annual_renewable_electricity_kwh | Annual_renewable_electricity_kwh_fraction | npv | lcc
Chicago | 25 | 33093 | 31631 | 0 | 0 | 0 | 227.185 | 19 | 31 | 503.09 | 30885 | 181 | 0 | 0 | 3011330 | 968.5348 | 968.5348 | 974.7684 | 24213.37 | 24369.21 | 0.01 | 160073.42 | 19491.75 | 249405.08 | 171877.89 | 337570.09 | 50286.34 | 616649.43 | 0 | 31607.73 | 0.01 | -144035.66 | 6128591.62
Chicago | 39 | 52158 | 49854 | 0 | 0 | 0 | 172.763 | 12 | 24 | 314.806 | 21608 | 191 | 0 | 0 | 2993088 | 964.9368 | 964.9368 | 974.7684 | 24123.42 | 24369.21 | 0.01 | 190890.6 | 13893.38 | 304624.52 | 199434.86 | 335525.13 | 50250.12 | 614568.25 | 0 | 49836.5 | 0.02 | -132257.9 | 6138763.69
Chicago | 39 | 52158 | 49854 | 0 | 0 | 0 | 149.191 | 12 | 24 | 314.806 | 21608 | 191 | 0 | 0 | 2993088 | 964.9368 | 964.9368 | 974.7684 | 24123.42 | 24369.21 | 0.01 | 190890.6 | 13893.38 | 304624.52 | 199434.86 | 335525.13 | 50250.12 | 614568.25 | 0 | 49838.89 | 0.02 | -113332.79 | 6139196.16

## MarkhamA_4
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Battery_initial_capex_cost | Grid_Electricity_Supplied_kWh_annual | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | LifeCycle_Emission_Reduction_Fraction | LifeCycle_capex_costs_for_generation_techs | LifeCycle_capex_costs_for_battery | Initial_upfront_capex_wo_incentives | Initial_upfront_capex_w_incentives | Yr1_energy_cost_after_tax | Yr1_demand_cost_after_tax | Yr1_total_energy_bill_before_tax | Yr1_export_benefit_before_tax | Annual_renewable_electricity_kwh | Annual_renewable_electricity_kwh_fraction | npv | lcc
Chicago | 743 | 983520 | 940067 | 0 | 0 | 0 | 6677.987 | 355 | 1854 | 121686.207 | 1167093.2 | 3632889 | 1092.1556 | 1092.1556 | 1066.8792 | 27303.89 | 26671.98 | -0.02 | 0 | 815036.81 | 1167092.93 | 533740.25 | 423231.59 | 100596.81 | 543011.4 | 0 | 939389.34 | 0.21 | -588084.67 | 6148985.22
Chicago | 743 | 983520 | 940067 | 0 | 0 | 0 | 6002.05 | 411 | 2948 | 235258.195 | 1715086.1 | 3645364 | 1116.6192 | 1116.6192 | 1066.8792 | 27915.48 | 26671.98 | -0.05 | 0 | 1222716.67 | 1715090.56 | 812282.27 | 424684.94 | 92913.73 | 536781.67 | 0 | 939457.91 | 0.21 | -895593.18 | 6496970.79
Chicago | 743 | 983520 | 940067 | 0 | 0 | 0 | 4931.872 | 411 | 4414 | 372791.924 | 2381783.95 | 3660427 | 1149.0628 | 1149.0628 | 1066.8792 | 28726.57 | 26671.98 | -0.08 | 0 | 1733705.7 | 2381785.35 | 1167928.93 | 426439.74 | 85792.7 | 531415.44 | 0 | 939566.47 | 0.21 | -1336155.71 | 6956539.73

## CermakA_19
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Battery_initial_capex_cost | Generator_size | Generator_annual_fuel_consumption | Generator_annual_energy_produced | Grid_Electricity_Supplied_kWh_annual | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | LifeCycle_Emission_Reduction_Fraction | LifeCycle_capex_costs_for_generation_techs | LifeCycle_capex_costs_for_battery | Initial_upfront_capex_wo_incentives | Initial_upfront_capex_w_incentives | Yr1_energy_cost_after_tax | Yr1_demand_cost_after_tax | Yr1_total_energy_bill_before_tax | Yr1_export_benefit_before_tax | Annual_renewable_electricity_kwh | Annual_renewable_electricity_kwh_fraction | npv | lcc
Chicago | 25 | 33093 | 31631 | 0 | 0 | 0 | 227.185 | 19 | 31 | 503.09 | 30885 | 180.96 | 0 | 0 | 3011330 | 968.5348 | 968.5348 | 974.7684 | 24213.37 | 24369.21 | 0.01 | 160073.42 | 19491.75 | 249405.08 | 171877.89 | 337570.09 | 50286.34 | 616649.43 | 0 | 31607.73 | 0.01 | -144035.66 | 6128591.62
Chicago | 39 | 52158 | 49854 | 0 | 0 | 0 | 172.763 | 12 | 24 | 314.806 | 21608 | 190.75 | 0 | 0 | 2993088 | 964.9368 | 964.9368 | 974.7684 | 24123.42 | 24369.21 | 0.01 | 190890.6 | 13893.38 | 304624.52 | 199434.86 | 335525.13 | 50250.12 | 614568.25 | 0 | 49836.5 | 0.02 | -132257.9 | 6138763.69
Chicago | 39 | 52158 | 49854 | 0 | 0 | 0 | 149.191 | 12 | 24 | 314.806 | 21608 | 190.75 | 0 | 0 | 2993088 | 964.9368 | 964.9368 | 974.7684 | 24123.42 | 24369.21 | 0.01 | 190890.6 | 13893.38 | 304624.52 | 199434.86 | 335525.13 | 50250.12 | 614568.25 | 0 | 49838.89 | 0.02 | -113332.79 | 6139196.16

## MarkhamA_5
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Battery_initial_capex_cost | Grid_Electricity_Supplied_kWh_annual | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | LifeCycle_Emission_Reduction_Fraction | LifeCycle_capex_costs_for_generation_techs | LifeCycle_capex_costs_for_battery | Initial_upfront_capex_wo_incentives | Initial_upfront_capex_w_incentives | Yr1_energy_cost_after_tax | Yr1_demand_cost_after_tax | Yr1_total_energy_bill_before_tax | Yr1_export_benefit_before_tax | Annual_renewable_electricity_kwh | Annual_renewable_electricity_kwh_fraction | npv | lcc
Chicago | 743 | 983520 | 940067 | 0 | 0 | 0 | 6677.987 | 355 | 1854 | 121686.207 | 1167093.2 | 3632889 | 1092.1556 | 1092.1556 | 1066.8792 | 27303.89 | 26671.98 | -0.02 | 0 | 815036.81 | 1167092.93 | 533740.25 | 423231.59 | 100596.81 | 543011.4 | 0 | 939389.34 | 0.21 | -588084.67 | 6148985.22
Chicago | 743 | 983520 | 940067 | 0 | 0 | 0 | 6002.05 | 411 | 2948 | 235258.195 | 1715086.1 | 3645364 | 1116.6192 | 1116.6192 | 1066.8792 | 27915.48 | 26671.98 | -0.05 | 0 | 1222716.67 | 1715090.56 | 812282.27 | 424684.94 | 92913.73 | 536781.67 | 0 | 939457.91 | 0.21 | -895593.18 | 6496970.79
Chicago | 743 | 983520 | 940067 | 0 | 0 | 0 | 4931.872 | 411 | 4414 | 372791.924 | 2381783.95 | 3660427 | 1149.0628 | 1149.0628 | 1066.8792 | 28726.57 | 26671.98 | -0.08 | 0 | 1733705.7 | 2381785.35 | 1167928.93 | 426439.74 | 85792.7 | 531415.44 | 0 | 939566.47 | 0.21 | -1336155.71 | 6956539.73

## ProvdientA_2
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Battery_initial_capex_cost | Grid_Electricity_Supplied_kWh_annual | Generator_size | Generator_annual_fuel_consumption | Generator_annual_energy_produced | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | LifeCycle_Emission_Reduction_Fraction | LifeCycle_capex_costs_for_generation_techs | LifeCycle_capex_costs_for_battery | Initial_upfront_capex_wo_incentives | Initial_upfront_capex_w_incentives | Yr1_energy_cost_after_tax | Yr1_demand_cost_after_tax | Yr1_total_energy_bill_before_tax | Yr1_export_benefit_before_tax | Annual_renewable_electricity_kwh | Annual_renewable_electricity_kwh_fraction | npv | lcc
Chicago | 38 | 50639 | 48402 | 0 | 0 | 0 | 65.358 | 10 | 13 | 154.426 | 14496 | 11323322 | 808 | 0 | 0 | 3631.5468 | 3631.5468 | 3641.0904 | 90788.67 | 91027.26 | 0 | 590306.34 | 8963.71 | 694245.1 | 595639.43 | 1319167.04 | 220602.28 | 1558952.32 | 0 | 48395.35 | 0 | -601719.55 | 15703993.52
Chicago | 38 | 50639 | 48402 | 0 | 0 | 0 | 75.307 | 10 | 13 | 154.426 | 14496 | 11323322 | 869 | 0 | 0 | 3631.5468 | 3631.5468 | 3641.0904 | 90788.67 | 91027.26 | 0 | 629582.59 | 8963.71 | 733521.35 | 634915.68 | 1319167.04 | 220602.28 | 1558952.32 | 0 | 48394.34 | 0 | -566729.71 | 15757096.46
Chicago | 38 | 50639 | 48402 | 0 | 0 | 0 | 70.024 | 10 | 13 | 154.426 | 14496 | 11323322 | 869 | 0 | 0 | 3631.5468 | 3631.5468 | 3641.0904 | 90788.67 | 91027.26 | 0 | 629582.59 | 8963.71 | 733521.35 | 634915.68 | 1319167.04 | 220602.28 | 1558952.32 | 0 | 48394.87 | 0 | -484663.97 | 15759016.71

## CermakA_20
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Battery_initial_capex_cost | Generator_size | Generator_annual_fuel_consumption | Generator_annual_energy_produced | Grid_Electricity_Supplied_kWh_annual | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | LifeCycle_Emission_Reduction_Fraction | LifeCycle_capex_costs_for_generation_techs | LifeCycle_capex_costs_for_battery | Initial_upfront_capex_wo_incentives | Initial_upfront_capex_w_incentives | Yr1_energy_cost_after_tax | Yr1_demand_cost_after_tax | Yr1_total_energy_bill_before_tax | Yr1_export_benefit_before_tax | Annual_renewable_electricity_kwh | Annual_renewable_electricity_kwh_fraction | npv | lcc
Chicago | 25 | 33093 | 31540 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0 | 0 | 3011373 | 968.5476 | 968.5476 | 974.7684 | 24213.69 | 24369.21 | 0.01 | 41313.56 | 0 | 100900 | 41313.56 | 337574.96 | 51798.68 | 618166.64 | 0 | 31540.23 | 0.01 | 1393.69 | 6901990.32
Chicago | 25 | 33093 | 31540 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0 | 0 | 3011373 | 968.5476 | 968.5476 | 974.7684 | 24213.69 | 24369.21 | 0.01 | 41313.56 | 0 | 100900 | 41313.56 | 337574.96 | 51798.68 | 618166.64 | 0 | 31540.23 | 0.01 | 1393.69 | 6902994.04
Chicago | 25 | 33093 | 31540 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 600 | 0 | 0 | 3011373 | 968.5476 | 968.5476 | 974.7684 | 24213.69 | 24369.21 | 0.01 | 41313.56 | 0 | 100900 | 41313.56 | 337574.96 | 51798.68 | 618166.64 | 0 | 31540.23 | 0.01 | 1393.69 | 6903879.22
Chicago | 25 | 33093 | 31540 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 3011373 | 968.5476 | 968.5476 | 974.7684 | 24213.69 | 24369.21 | 0.01 | 41313.56 | 0 | 100900 | 41313.56 | 337574.96 | 51798.68 | 618166.64 | 0 | 31540.23 | 0.01 | 1393.69 | 6830597.62
Chicago | 25 | 33093 | 31540 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 3011373 | 968.5476 | 968.5476 | 974.7684 | 24213.69 | 24369.21 | 0.01 | 41313.56 | 0 | 100900 | 41313.56 | 337574.96 | 51798.68 | 618166.64 | 0 | 31540.23 | 0.01 | 1393.69 | 6831099.48
Chicago | 25 | 33093 | 31540 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 3011373 | 968.5476 | 968.5476 | 974.7684 | 24213.69 | 24369.21 | 0.01 | 41313.56 | 0 | 100900 | 41313.56 | 337574.96 | 51798.68 | 618166.64 | 0 | 31540.23 | 0.01 | 1393.69 | 6831542.07

## MarkhamA_6
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Battery_initial_capex_cost | Grid_Electricity_Supplied_kWh_annual | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | LifeCycle_Emission_Reduction_Fraction | LifeCycle_capex_costs_for_generation_techs | LifeCycle_capex_costs_for_battery | Initial_upfront_capex_wo_incentives | Initial_upfront_capex_w_incentives | Yr1_energy_cost_after_tax | Yr1_demand_cost_after_tax | Yr1_total_energy_bill_before_tax | Yr1_export_benefit_before_tax | Annual_renewable_electricity_kwh | Annual_renewable_electricity_kwh_fraction | npv | lcc
Chicago | 743 | 983520 | 937376 | 0 | 0 | 0 | 5463.151 | 711 | 3709 | 311557.023 | 2334186.4 | 3656428 | 1134.9116 | 1134.9116 | 1067.41 | 28372.79 | 26685.25 | -0.06 | 0 | 1713820.79 | 2334185.86 | 1041031.41 | 425973.88 | 88944.96 | 534101.84 | 0 | 936821.6 | 0.21 | -1329248.1 | 7671723.22
Chicago | 743 | 983520 | 937376 | 0 | 0 | 0 | 8457.886 | 830 | 7322 | 489211.26 | 4086696.25 | 3675340 | 1171.766 | 1171.766 | 1067.41 | 29294.15 | 26685.25 | -0.1 | 0 | 3091082.76 | 4086696.01 | 1926210.57 | 428177.16 | 80416.11 | 527776.27 | 0 | 936517.81 | 0.21 | -2546081.7 | 8980296.86
Chicago | 743 | 983520 | 937376 | 0 | 0 | 0 | 18277.023 | 830 | 10437 | 565568.032 | 5504326.1 | 3682974 | 1180.5832 | 1180.5832 | 1067.41 | 29514.58 | 26685.25 | -0.11 | 0 | 4226262.76 | 5504326.21 | 2666378.35 | 429066.52 | 77070.71 | 525320.23 | 0 | 935521.76 | 0.21 | -3611514.52 | 10088807.14
Chicago | 743 | 983520 | 937376 | 0 | 0 | 0 | 6678.349 | 355 | 1854 | 121856.234 | 1167093.2 | 3635599 | 1092.7448 | 1092.7448 | 1067.41 | 27318.62 | 26685.25 | -0.02 | 0 | 856910.39 | 1167092.93 | 520515.71 | 423547.33 | 100681.77 | 543412.1 | 0 | 936698.33 | 0.21 | -599229.49 | 6915911.41
Chicago | 743 | 983520 | 937376 | 0 | 0 | 0 | 5995.566 | 411 | 2952 | 236015.402 | 1716965.25 | 3648139 | 1117.3464 | 1117.3464 | 1067.41 | 27933.66 | 26685.25 | -0.05 | 0 | 1285170.19 | 1716964.49 | 793820.21 | 425008.25 | 92962.36 | 537153.61 | 0 | 936767.59 | 0.21 | -913659.33 | 7276211.27
Chicago | 743 | 983520 | 937376 | 0 | 0 | 0 | 4933.978 | 411 | 4418 | 373624.515 | 2383899.7 | 3663210 | 1149.8216 | 1149.8216 | 1067.41 | 28745.54 | 26685.25 | -0.08 | 0 | 1819224.53 | 2383899.74 | 1142037.94 | 426764.02 | 85836.4 | 531783.42 | 0 | 936875.28 | 0.21 | -1367860.92 | 7751951.6

## ProvidentA_3
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Battery_initial_capex_cost | Grid_Electricity_Supplied_kWh_annual | Generator_size | Generator_annual_fuel_consumption | Generator_annual_energy_produced | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | LifeCycle_Emission_Reduction_Fraction | LifeCycle_capex_costs_for_generation_techs | LifeCycle_capex_costs_for_battery | Initial_upfront_capex_wo_incentives | Initial_upfront_capex_w_incentives | Yr1_energy_cost_after_tax | Yr1_demand_cost_after_tax | Yr1_total_energy_bill_before_tax | Yr1_export_benefit_before_tax | Annual_renewable_electricity_kwh | Annual_renewable_electricity_kwh_fraction | npv | lcc
Chicago | 191 | 252399 | 240557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11131153 | 2192 | 0 | 0 | 3593.6436 | 3593.6436 | 3641.0904 | 89841.09 | 91027.26 | 0.01 | 315098.81 | 0 | 769565.05 | 315098.81 | 1296779.34 | 216008.71 | 1531971.05 | 0 | 240557.61 | 0.02 | 31360.16 | 17513321.76
Chicago | 191 | 252399 | 240557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11131153 | 2192 | 0 | 0 | 3593.6436 | 3593.6436 | 3641.0904 | 89841.09 | 91027.26 | 0.01 | 315098.81 | 0 | 769565.05 | 315098.81 | 1296779.34 | 216008.71 | 1531971.05 | 0 | 240557.61 | 0.02 | 31606.91 | 17517103.29
Chicago | 191 | 252399 | 240557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11131153 | 1590 | 0 | 0 | 3593.6436 | 3593.6436 | 3641.0904 | 89841.09 | 91027.26 | 0.01 | 635899.81 | 0 | 1090366.05 | 635899.81 | 1296779.34 | 216008.71 | 1531971.05 | 0 | 240557.61 | 0.02 | -352056.77 | 17691615.29
Chicago | 239 | 316345 | 301503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11070208 | 1610 | 0 | 0 | 3581.6232 | 3581.6232 | 3641.0904 | 89540.58 | 91027.26 | 0.02 | 728898.3 | 0 | 1298503.43 | 728898.3 | 1289679.22 | 214958.87 | 1523821.09 | 0 | 301502.81 | 0.03 | -301755.75 | 17714907.15
Chicago | 191 | 252399 | 240557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11131153 | 1096 | 0 | 0 | 3593.6436 | 3593.6436 | 3641.0904 | 89841.09 | 91027.26 | 0.01 | 315098.81 | 0 | 769565.05 | 315098.81 | 1296779.34 | 216008.71 | 1531971.05 | 0 | 240557.61 | 0.02 | 31646.26 | 17255864.12

## ProvdientA_4
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Battery_initial_capex_cost | Grid_Electricity_Supplied_kWh_annual | Generator_size | Generator_annual_fuel_consumption | Generator_annual_energy_produced | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | LifeCycle_Emission_Reduction_Fraction | LifeCycle_capex_costs_for_generation_techs | LifeCycle_capex_costs_for_battery | Initial_upfront_capex_wo_incentives | Initial_upfront_capex_w_incentives | Yr1_energy_cost_after_tax | Yr1_demand_cost_after_tax | Yr1_total_energy_bill_before_tax | Yr1_export_benefit_before_tax | Annual_renewable_electricity_kwh | Annual_renewable_electricity_kwh_fraction | npv | lcc
Chicago | 191 | 252399 | 240557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11131153 | 2192 | 0 | 0 | 3593.6436 | 3593.6436 | 3641.0904 | 89841.09 | 91027.26 | 0.01 | 315098.81 | 0 | 769565.05 | 315098.81 | 1296779.34 | 216008.71 | 1531971.05 | 0 | 240557.61 | 0.02 | 31360.16 | 17513321.76
Chicago | 191 | 252399 | 240557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11131153 | 2192 | 0 | 0 | 3593.6436 | 3593.6436 | 3641.0904 | 89841.09 | 91027.26 | 0.01 | 315098.81 | 0 | 769565.05 | 315098.81 | 1296779.34 | 216008.71 | 1531971.05 | 0 | 240557.61 | 0.02 | 31606.91 | 17517103.29
Chicago | 191 | 252399 | 240557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11131153 | 1590 | 0 | 0 | 3593.6436 | 3593.6436 | 3641.0904 | 89841.09 | 91027.26 | 0.01 | 635899.81 | 0 | 1090366.05 | 635899.81 | 1296779.34 | 216008.71 | 1531971.05 | 0 | 240557.61 | 0.02 | -352056.77 | 17691615.29
Chicago | 239 | 316345 | 301503 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11070208 | 1610 | 0 | 0 | 3581.6232 | 3581.6232 | 3641.0904 | 89540.58 | 91027.26 | 0.02 | 728898.3 | 0 | 1298503.43 | 728898.3 | 1289679.22 | 214958.87 | 1523821.09 | 0 | 301502.81 | 0.03 | -301755.75 | 17714907.15
Chicago | 191 | 252399 | 240557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11131153 | 1096 | 0 | 0 | 3593.6436 | 3593.6436 | 3641.0904 | 89841.09 | 91027.26 | 0.01 | 315098.81 | 0 | 769565.05 | 315098.81 | 1296779.34 | 216008.71 | 1531971.05 | 0 | 240557.61 | 0.02 | 31646.26 | 17255864.12

## ProvdientA_5
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Battery_initial_capex_cost | Grid_Electricity_Supplied_kWh_annual | Generator_size | Generator_annual_fuel_consumption | Generator_annual_energy_produced | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | LifeCycle_Emission_Reduction_Fraction | LifeCycle_capex_costs_for_generation_techs | LifeCycle_capex_costs_for_battery | Initial_upfront_capex_wo_incentives | Initial_upfront_capex_w_incentives | Yr1_energy_cost_after_tax | Yr1_demand_cost_after_tax | Yr1_total_energy_bill_before_tax | Yr1_export_benefit_before_tax | Annual_renewable_electricity_kwh | Annual_renewable_electricity_kwh_fraction | npv | lcc
Chicago | 131 | 173354 | 165221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11206490 | 2192 | 0 | 0 | 3608.5028 | 3608.5028 | 3641.0904 | 90212.57 | 91027.26 | 0.01 | 216416.94 | 0 | 528554.56 | 216416.94 | 1305556.13 | 218066.67 | 1542805.8 | 0 | 165220.37 | 0.01 | 25098.27 | 17519583.65
Chicago | 131 | 173354 | 165221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11206490 | 2192 | 0 | 0 | 3608.5028 | 3608.5028 | 3641.0904 | 90212.57 | 91027.26 | 0.01 | 216416.94 | 0 | 528554.56 | 216416.94 | 1305556.13 | 218066.67 | 1542805.8 | 0 | 165220.37 | 0.01 | 25267.75 | 17523442.46

## ProvdientA_7
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Battery_initial_capex_cost | Grid_Electricity_Supplied_kWh_annual | Generator_size | Generator_annual_fuel_consumption | Generator_annual_energy_produced | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | LifeCycle_Emission_Reduction_Fraction | LifeCycle_capex_costs_for_generation_techs | LifeCycle_capex_costs_for_battery | Initial_upfront_capex_wo_incentives | Initial_upfront_capex_w_incentives | Yr1_energy_cost_after_tax | Yr1_demand_cost_after_tax | Yr1_total_energy_bill_before_tax | Yr1_export_benefit_before_tax | Annual_renewable_electricity_kwh | Annual_renewable_electricity_kwh_fraction | npv | lcc
Chicago | 131 | 173354 | 165221 | 0 | 0 | 0 | 0 | 16 | 20 | 231.21 | 23469 | 11206510 | 2000 | 0 | 0 | 3608.5076 | 3608.5076 | 3641.0904 | 90212.69 | 91027.26 | 0.01 | 216416.94 | 15398.93 | 552026.61 | 224785.97 | 1305558.41 | 216349.55 | 1541090.96 | 0 | 165220.37 | 0.01 | 28320.49 | 17470945.24
Chicago | 131 | 173354 | 165221 | 0 | 0 | 0 | 0 | 16 | 20 | 231.21 | 23469 | 11206510 | 2000 | 0 | 0 | 3608.5076 | 3608.5076 | 3641.0904 | 90212.69 | 91027.26 | 0.01 | 216416.94 | 15398.93 | 552026.61 | 224785.97 | 1305558.41 | 216349.55 | 1541090.96 | 0 | 165220.37 | 0.01 | 28489.97 | 17474804.05

## ProvdientA_8
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Battery_initial_capex_cost | Grid_Electricity_Supplied_kWh_annual | Generator_size | Generator_annual_fuel_consumption | Generator_annual_energy_produced | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | LifeCycle_Emission_Reduction_Fraction | LifeCycle_capex_costs_for_generation_techs | LifeCycle_capex_costs_for_battery | Initial_upfront_capex_wo_incentives | Initial_upfront_capex_w_incentives | Yr1_energy_cost_after_tax | Yr1_demand_cost_after_tax | Yr1_total_energy_bill_before_tax | Yr1_export_benefit_before_tax | Annual_renewable_electricity_kwh | Annual_renewable_electricity_kwh_fraction | npv | lcc
Chicago | 131 | 173354 | 165221 | 0 | 0 | 0 | 0 | 16 | 20 | 231.21 | 23469 | 11206510 | 2192 | 0 | 0 | 3608.5076 | 3608.5076 | 3641.0904 | 90212.69 | 91027.26 | 0.01 | 216416.94 | 15398.93 | 552026.61 | 224785.97 | 1305558.41 | 216349.55 | 1541090.96 | 0 | 165220.37 | 0.01 | 28320.49 | 17516361.43
Chicago | 131 | 173354 | 165221 | 0 | 0 | 0 | 0 | 16 | 20 | 231.21 | 23469 | 11206510 | 2192 | 0 | 0 | 3608.5076 | 3608.5076 | 3641.0904 | 90212.69 | 91027.26 | 0.01 | 216416.94 | 15398.93 | 552026.61 | 224785.97 | 1305558.41 | 216349.55 | 1541090.96 | 0 | 165220.37 | 0.01 | 28489.97 | 17520220.23
Chicago | 131 | 173354 | 165221 | 0 | 0 | 0 | 0 | 39 | 66 | 886.405 | 65302 | 11206569 | 1556 | 0 | 0 | 3608.5496 | 3608.5496 | 3641.0904 | 90213.74 | 91027.26 | 0.01 | 515339.53 | 43864.95 | 892777.86 | 539794.47 | 1305565.34 | 214429.32 | 1539177.66 | 0 | 165220.37 | 0.01 | -332928.38 | 17672486.9
Chicago | 131 | 173354 | 165221 | 0 | 0 | 0 | 0 | 32 | 76 | 933.142 | 63404 | 11206572 | 1639 | 0 | 0 | 3608.5552 | 3608.5552 | 3641.0904 | 90213.88 | 91027.26 | 0.01 | 569059.86 | 43874.36 | 944603.13 | 594272.34 | 1305565.59 | 214367.95 | 1539116.54 | 0 | 165220.37 | 0.01 | -335806.03 | 17748957.43
Chicago | 131 | 173354 | 165221 | 0 | 0 | 0 | 0 | 16 | 20 | 231.21 | 23469 | 11206510 | 1096 | 0 | 0 | 3608.5076 | 3608.5076 | 3641.0904 | 90212.69 | 91027.26 | 0.01 | 216416.94 | 15398.93 | 552026.61 | 224785.97 | 1305558.41 | 216349.55 | 1541090.96 | 0 | 165220.37 | 0.01 | 30751.3 | 17260724.51

## ProvdientA_9
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Battery_initial_capex_cost | Grid_Electricity_Supplied_kWh_annual | Generator_size | Generator_annual_fuel_consumption | Generator_annual_energy_produced | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | LifeCycle_Emission_Reduction_Fraction | LifeCycle_capex_costs_for_generation_techs | LifeCycle_capex_costs_for_battery | Initial_upfront_capex_wo_incentives | Initial_upfront_capex_w_incentives | Yr1_energy_cost_after_tax | Yr1_demand_cost_after_tax | Yr1_total_energy_bill_before_tax | Yr1_export_benefit_before_tax | Annual_renewable_electricity_kwh | Annual_renewable_electricity_kwh_fraction | npv | lcc
Chicago | 131 | 173354 | 165221 | 0 | 0 | 0 | 0 | 16 | 20 | 231.21 | 23469 | 11206510 | 2192 | 0 | 0 | 3608.5076 | 3608.5076 | 3641.0904 | 90212.69 | 91027.26 | 0.01 | 216416.94 | 15398.93 | 552026.61 | 224785.97 | 1305558.41 | 216349.55 | 1541090.96 | 0 | 165220.37 | 0.01 | 28320.49 | 17516361.43
Chicago | 131 | 173354 | 165221 | 0 | 0 | 0 | 0 | 16 | 20 | 231.21 | 23469 | 11206510 | 2192 | 0 | 0 | 3608.5076 | 3608.5076 | 3641.0904 | 90212.69 | 91027.26 | 0.01 | 216416.94 | 15398.93 | 552026.61 | 224785.97 | 1305558.41 | 216349.55 | 1541090.96 | 0 | 165220.37 | 0.01 | 28489.97 | 17520220.23
Chicago | 131 | 173354 | 165221 | 0 | 0 | 0 | 0 | 39 | 66 | 886.405 | 65302 | 11206569 | 1556 | 0 | 0 | 3608.5496 | 3608.5496 | 3641.0904 | 90213.74 | 91027.26 | 0.01 | 515339.53 | 43864.95 | 892777.86 | 539794.47 | 1305565.34 | 214429.32 | 1539177.66 | 0 | 165220.37 | 0.01 | -332928.38 | 17672486.9
Chicago | 131 | 173354 | 165221 | 0 | 0 | 0 | 0 | 32 | 76 | 933.142 | 63404 | 11206572 | 1639 | 0 | 0 | 3608.5552 | 3608.5552 | 3641.0904 | 90213.88 | 91027.26 | 0.01 | 569059.86 | 43874.36 | 944603.13 | 594272.34 | 1305565.59 | 214367.95 | 1539116.54 | 0 | 165220.37 | 0.01 | -335806.03 | 17748957.43
Chicago | 131 | 173354 | 165221 | 0 | 0 | 0 | 0 | 159 | 2566 | 41877.049 | 1312520 | 11210406 | 1096 | 0 | 0 | 3613.6204 | 3613.6204 | 3641.0904 | 90340.51 | 91027.26 | 0.01 | 216416.94 | 1016200.9 | 1841075.61 | 861875.52 | 1306012.28 | 199855.16 | 1525050.44 | 0 | 165220.37 | 0.01 | -752491.06 | 18087788.5

## ProvdientA_12
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Battery_initial_capex_cost | Grid_Electricity_Supplied_kWh_annual | Generator_size | Generator_annual_fuel_consumption | Generator_annual_energy_produced | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | LifeCycle_Emission_Reduction_Fraction | LifeCycle_capex_costs_for_generation_techs | LifeCycle_capex_costs_for_battery | Initial_upfront_capex_wo_incentives | Initial_upfront_capex_w_incentives | Yr1_energy_cost_after_tax | Yr1_demand_cost_after_tax | Yr1_total_energy_bill_before_tax | Yr1_export_benefit_before_tax | Annual_renewable_electricity_kwh | Annual_renewable_electricity_kwh_fraction | npv | lcc
Chicago | 131 | 173354 | 165221 | 0 | 0 | 0 | 0 | 16 | 20 | 231.21 | 23469 | 11206510 | 2192 | 0 | 0 | 3608.5076 | 3608.5076 | 3641.0904 | 90212.69 | 91027.26 | 0.01 | 216416.94 | 15398.93 | 552026.61 | 224785.97 | 1305558.41 | 216349.55 | 1541090.96 | 0 | 165220.37 | 0.01 | 28320.49 | 17516361.43
Chicago | 131 | 173354 | 165221 | 0 | 0 | 0 | 0 | 16 | 20 | 231.21 | 23469 | 11206510 | 2192 | 0 | 0 | 3608.5076 | 3608.5076 | 3641.0904 | 90212.69 | 91027.26 | 0.01 | 216416.94 | 15398.93 | 552026.61 | 224785.97 | 1305558.41 | 216349.55 | 1541090.96 | 0 | 165220.37 | 0.01 | 28489.97 | 17520220.23
Chicago | 131 | 173354 | 165221 | 0 | 0 | 0 | 0 | 150 | 88 | 1205.139 | 176663 | 11206598 | 1553 | 0 | 0 | 3608.5812 | 3608.5812 | 3641.0904 | 90214.53 | 91027.26 | 0.01 | 513611.75 | 108687.1 | 1002410.1 | 568349.2 | 1305568.72 | 213824.88 | 1538576.6 | 0 | 165220.37 | 0.01 | -388860.94 | 17728419.46
Chicago | 131 | 173354 | 165221 | 0 | 0 | 0 | 0 | 150 | 140 | 1991.995 | 200246 | 11206671 | 1626 | 0 | 0 | 3608.6752 | 3608.6752 | 3641.0904 | 90216.88 | 91027.26 | 0.01 | 561187.09 | 127572.32 | 1073569.59 | 628238.2 | 1305577.16 | 212741.18 | 1537501.34 | 0 | 165220.37 | 0.01 | -391209.07 | 17804360.47
Chicago | 131 | 173354 | 165221 | 0 | 0 | 0 | 0 | 159 | 2566 | 41877.049 | 1312520 | 11210406 | 1096 | 0 | 0 | 3613.6204 | 3613.6204 | 3641.0904 | 90340.51 | 91027.26 | 0.01 | 216416.94 | 1016200.9 | 1841075.61 | 861875.52 | 1306012.28 | 199855.16 | 1525050.44 | 0 | 165220.37 | 0.01 | -752491.06 | 18087788.5

## ProvdientA_15
City | PV_size | PV_year1_production | PV_annual_energy_production_avg | PV_energy_lcoe | PV_energy_exported | PV_energy_curtailed | PV_energy_to_Battery_year1 | Battery_size_kW | Battery_size_kWh | Battery_serve_electric_load | Battery_initial_capex_cost | Grid_Electricity_Supplied_kWh_annual | Generator_size | Generator_annual_fuel_consumption | Generator_annual_energy_produced | Total_Annual_Emissions_CO2 | ElecUtility_Annual_Emissions_CO2 | BAU_Total_Annual_Emissions_CO2 | LifeCycle_Emissions_CO2 | BAU_LifeCycle_Emissions_CO2 | LifeCycle_Emission_Reduction_Fraction | LifeCycle_capex_costs_for_generation_techs | LifeCycle_capex_costs_for_battery | Initial_upfront_capex_wo_incentives | Initial_upfront_capex_w_incentives | Yr1_energy_cost_after_tax | Yr1_demand_cost_after_tax | Yr1_total_energy_bill_before_tax | Yr1_export_benefit_before_tax | Annual_renewable_electricity_kwh | Annual_renewable_electricity_kwh_fraction | npv | lcc
Chicago | 131 | 173354 | 165221 | 0 | 0 | 0 | 0 | 16 | 20 | 231.21 | 23469 | 11206510 | 2192 | 0 | 0 | 3608.5076 | 3608.5076 | 3641.0904 | 90212.69 | 91027.26 | 0.01 | 216416.94 | 15398.93 | 552026.61 | 224785.97 | 1305558.41 | 216349.55 | 1541090.96 | 0 | 165220.37 | 0.01 | 28320.49 | 17516361.43
Chicago | 131 | 173354 | 165221 | 0 | 0 | 0 | 0 | 16 | 20 | 231.21 | 23469 | 11206510 | 2192 | 0 | 0 | 3608.5076 | 3608.5076 | 3641.0904 | 90212.69 | 91027.26 | 0.01 | 216416.94 | 15398.93 | 552026.61 | 224785.97 | 1305558.41 | 216349.55 | 1541090.96 | 0 | 165220.37 | 0.01 | 28489.97 | 17520220.23
Chicago | 131 | 173354 | 165221 | 0 | 0 | 0 | 0 | 150 | 88 | 1205.139 | 176663 | 11206598 | 1553 | 0 | 0 | 3608.5812 | 3608.5812 | 3641.0904 | 90214.53 | 91027.26 | 0.01 | 513611.75 | 108687.1 | 1002410.1 | 568349.2 | 1305568.72 | 213824.88 | 1538576.6 | 0 | 165220.37 | 0.01 | -388860.94 | 17728419.46
Chicago | 131 | 173354 | 165221 | 0 | 0 | 0 | 0 | 150 | 140 | 1991.995 | 200246 | 11206671 | 1626 | 0 | 0 | 3608.6752 | 3608.6752 | 3641.0904 | 90216.88 | 91027.26 | 0.01 | 561187.09 | 127572.32 | 1073569.59 | 628238.2 | 1305577.16 | 212741.18 | 1537501.34 | 0 | 165220.37 | 0.01 | -391209.07 | 17804360.47
Chicago | 131 | 173354 | 165221 | 0 | 0 | 0 | 0 | 159 | 2566 | 41877.049 | 1312520 | 11210406 | 1096 | 0 | 0 | 3613.6204 | 3613.6204 | 3641.0904 | 90340.51 | 91027.26 | 0.01 | 216416.94 | 1016200.9 | 1841075.61 | 861875.52 | 1306012.28 | 199855.16 | 1525050.44 | 0 | 165220.37 | 0.01 | -752491.06 | 18087788.5

## CermakA_21
City | PV Size (kW) | PV Year 1 Production (kWh) | Annual Energy Production from PV (kWh) | PV Energy LCOE | Exported Energy to Grid from PV Production (kWh) | Energy Produced from PV curtailed (kWh) | Energy to Battery from PV production (kWh) | Battery Size (kW) | Battery Size (kWh) | Battery Serving Electric Load (kWh) | Battery Initial CapEx Cost ($) | Annual Energy Supplied by Grid for Electric Load (kWh) | Generator Size (kW) | Annual Fuel Consumption by Generator (MMBtu) | Annual Energy Produced by Generator (kWh) | Total Annual Emissions CO2 | Electric Utility Annual Emissions CO2 (tonnes) | BAU Total Annual Emissions CO2 (tonnes) | LifeCycle Emissions CO2 (tonnes) | BAU LifeCycle Emissions CO2 (tonnes) | LifeCycle Emission Reduction Fraction (%) | LifeCycle CapEx Costs for Energy Generation Technologies ($) | LifeCycle CapEx Costs for Energy Storage Technologies ($) | Initial Upfront CapEx w/o Incentives ($) | Initial Upfront CapEx w/ Incentives | Year 1 Energy Cost after tax ($) | Year 1 Demand Charges Costs after tax ($) | Year 1 Total Energy Bill before tax ($) | Year 1 Financial Benefit from Exporting Energy before tax ($) | Annual Consumption of Electricity from Renewable Sources (kWh) | Annual Consumption of Electricity from Renewable Sources fraction (%) | Net Present Value (NPV) ($) | LifeCycle Costs (LCC) ($)
Chicago | 25 | 33093 | 31540 | 0 | 0 | 0 | 75.198 | 10 | 13 | 174.498 | 15101 | 600 | 0 | 0 | 3011389 | 968.5496 | 968.5496 | 974.7684 | 24213.74 | 24369.21 | 1% | 41313.56 | 9906.38 | 115999.95 | 46697.49 | 337576.7 | 50886.84 | 617256.54 | 0 | 31532.61 | 0.01 | 1373.7 | 6902010.31
Chicago | 25 | 33093 | 31540 | 0 | 0 | 0 | 95.685 | 10 | 13 | 174.498 | 15101 | 600 | 0 | 0 | 3011389 | 968.5496 | 968.5496 | 974.7684 | 24213.74 | 24369.21 | 1% | 41313.56 | 9906.38 | 115999.95 | 46697.49 | 337576.7 | 50886.84 | 617256.54 | 0 | 31530.53 | 0.01 | 1373.7 | 6903014.03
Chicago | 25 | 33093 | 31540 | 0 | 0 | 0 | 80.214 | 10 | 13 | 174.498 | 15101 | 600 | 0 | 0 | 3011389 | 968.5496 | 968.5496 | 974.7684 | 24213.74 | 24369.21 | 1% | 41313.56 | 9906.38 | 115999.95 | 46697.49 | 337576.7 | 50886.84 | 617256.54 | 0 | 31532.1 | 0.01 | 1373.7 | 6903899.21
Chicago | 25 | 33093 | 31540 | 0 | 0 | 0 | 1678.098 | 108 | 532 | 26313.091 | 340404 | 300 | 0 | 0 | 3014176 | 973.4464 | 973.4464 | 974.7684 | 24336.16 | 24369.21 | 0% | 41313.56 | 248958.95 | 441303.82 | 192016.43 | 337889.08 | 45574.28 | 612256.36 | 0 | 31370.01 | 0.01 | -175987.47 | 7015658.4
Chicago | 175 | 231650 | 220782 | 0 | 0 | 0 | 11206.554 | 80 | 684 | 30371.475 | 383456 | 300 | 0 | 0 | 2825344 | 929.9588 | 929.9588 | 974.7684 | 23248.97 | 24369.21 | 5% | 289194.9 | 289655.95 | 1089754.62 | 469496.09 | 316721.1 | 43787.56 | 589301.66 | 0 | 219644.85 | 0.07 | -232704.66 | 7087616.88
Chicago | 175 | 231650 | 220782 | 0 | 0 | 0 | 19420.176 | 80 | 1139 | 43553.312 | 590617 | 300 | 0 | 0 | 2826688 | 928.0316 | 928.0316 | 974.7684 | 23200.79 | 24369.21 | 5% | 289194.9 | 455541.51 | 1296915.06 | 577657.92 | 316871.77 | 43236.64 | 588901.41 | 0 | 218811.66 | 0.07 | -385590.68 | 7249868.97

## MarkhamA_7
City | PV Size (kW) | PV Year 1 Production (kWh) | Annual Energy Production from PV (kWh) | PV Energy LCOE | Exported Energy to Grid from PV Production (kWh) | Energy Produced from PV curtailed (kWh) | Energy to Battery from PV production (kWh) | Battery Size (kW) | Battery Size (kWh) | Battery Serving Electric Load (kWh) | Battery Initial CapEx Cost ($) | Annual Energy Supplied by Grid for Electric Load (kWh) | Total Annual Emissions CO2 | Electric Utility Annual Emissions CO2 (tonnes) | BAU Total Annual Emissions CO2 (tonnes) | LifeCycle Emissions CO2 (tonnes) | BAU LifeCycle Emissions CO2 (tonnes) | LifeCycle Emission Reduction Fraction (%) | LifeCycle CapEx Costs for Energy Generation Technologies ($) | LifeCycle CapEx Costs for Energy Storage Technologies ($) | Initial Upfront CapEx w/o Incentives ($) | Initial Upfront CapEx w/ Incentives | Year 1 Energy Cost after tax ($) | Year 1 Demand Charges Costs after tax ($) | Year 1 Total Energy Bill before tax ($) | Year 1 Financial Benefit from Exporting Energy before tax ($) | Annual Consumption of Electricity from Renewable Sources (kWh) | Annual Consumption of Electricity from Renewable Sources fraction (%) | Net Present Value (NPV) ($) | LifeCycle Costs (LCC) ($)
Chicago | 743 | 983520 | 937376 | 0 | 0 | 0 | 5463.151 | 711 | 3709 | 311557.023 | 2334186.4 | 3656428 | 1134.9116 | 1134.9116 | 1067.41 | 28372.79 | 26685.25 | -6% | 0 | 1713820.79 | 2334185.86 | 1041031.41 | 425973.88 | 88944.96 | 534101.84 | 0 | 936821.6 | 21% | -1329248.1 | 7671723.22
Chicago | 743 | 983520 | 937376 | 0 | 0 | 0 | 8457.886 | 830 | 7322 | 489211.26 | 4086696.25 | 3675340 | 1171.766 | 1171.766 | 1067.41 | 29294.15 | 26685.25 | -10% | 0 | 3091082.76 | 4086696.01 | 1926210.57 | 428177.16 | 80416.11 | 527776.27 | 0 | 936517.81 | 21% | -2546081.7 | 8980296.86
Chicago | 743 | 983520 | 937376 | 0 | 0 | 0 | 18277.023 | 830 | 10437 | 565568.032 | 5504326.1 | 3682974 | 1180.5832 | 1180.5832 | 1067.41 | 29514.58 | 26685.25 | -11% | 0 | 4226262.76 | 5504326.21 | 2666378.35 | 429066.52 | 77070.71 | 525320.23 | 0 | 935521.76 | 21% | -3611514.52 | 10088807.14
Chicago | 743 | 983520 | 937376 | 0 | 0 | 0 | 6678.349 | 355 | 1854 | 121856.234 | 1167093.2 | 3635599 | 1092.7448 | 1092.7448 | 1067.41 | 27318.62 | 26685.25 | -2% | 0 | 856910.39 | 1167092.93 | 520515.71 | 423547.33 | 100681.77 | 543412.1 | 0 | 936698.33 | 21% | -599229.49 | 6915911.41
Chicago | 743 | 983520 | 937376 | 0 | 0 | 0 | 5995.566 | 411 | 2952 | 236015.402 | 1716965.25 | 3648139 | 1117.3464 | 1117.3464 | 1067.41 | 27933.66 | 26685.25 | -5% | 0 | 1285170.19 | 1716964.49 | 793820.21 | 425008.25 | 92962.36 | 537153.61 | 0 | 936767.59 | 21% | -913659.33 | 7276211.27
Chicago | 743 | 983520 | 937376 | 0 | 0 | 0 | 4933.978 | 411 | 4418 | 373624.515 | 2383899.7 | 3663210 | 1149.8216 | 1149.8216 | 1067.41 | 28745.54 | 26685.25 | -8% | 0 | 1819224.53 | 2383899.74 | 1142037.94 | 426764.02 | 85836.4 | 531783.42 | 0 | 936875.28 | 21% | -1367860.92 | 7751951.6
this means that emissions grew

## ProvdientA_16
City | PV Size (kW) | PV Year 1 Production (kWh) | Annual Energy Production from PV (kWh) | PV Energy LCOE | Exported Energy to Grid from PV Production (kWh) | Energy Produced from PV curtailed (kWh) | Energy to Battery from PV production (kWh) | Battery Size (kW) | Battery Size (kWh) | Battery Serving Electric Load (kWh) | Battery Initial CapEx Cost ($) | Annual Energy Supplied by Grid for Electric Load (kWh) | Generator Size (kW) | Annual Fuel Consumption by Generator (MMBtu) | Annual Energy Produced by Generator (kWh) | Total Annual Emissions CO2 | Electric Utility Annual Emissions CO2 (tonnes) | BAU Total Annual Emissions CO2 (tonnes) | LifeCycle Emissions CO2 (tonnes) | BAU LifeCycle Emissions CO2 (tonnes) | LifeCycle Emission Reduction Fraction (%) | LifeCycle CapEx Costs for Energy Generation Technologies ($) | LifeCycle CapEx Costs for Energy Storage Technologies ($) | Initial Upfront CapEx w/o Incentives ($) | Initial Upfront CapEx w/ Incentives | Year 1 Energy Cost after tax ($) | Year 1 Demand Charges Costs after tax ($) | Year 1 Total Energy Bill before tax ($) | Year 1 Financial Benefit from Exporting Energy before tax ($) | Annual Consumption of Electricity from Renewable Sources (kWh) | Annual Consumption of Electricity from Renewable Sources fraction (%) | Net Present Value (NPV) ($) | LifeCycle Costs (LCC) ($)
Chicago | 131 | 173354 | 165221 | 0 | 0 | 0 | 0 | 16 | 20 | 231.21 | 23469 | 11206510 | 2192 | 0 | 0 | 3608.5076 | 3608.5076 | 3641.0904 | 90212.69 | 91027.26 | 1% | 216416.94 | 15398.93 | 552026.61 | 224785.97 | 1305558.41 | 216349.55 | 1541090.96 | 0 | 165220.37 | 1% | 28320.49 | 17516361.43
Chicago | 131 | 173354 | 165221 | 0 | 0 | 0 | 0 | 16 | 20 | 231.21 | 23469 | 11206510 | 2192 | 0 | 0 | 3608.5076 | 3608.5076 | 3641.0904 | 90212.69 | 91027.26 | 1% | 216416.94 | 15398.93 | 552026.61 | 224785.97 | 1305558.41 | 216349.55 | 1541090.96 | 0 | 165220.37 | 1% | 28489.97 | 17520220.23
Chicago | 131 | 173354 | 165221 | 0 | 0 | 0 | 0 | 39 | 66 | 886.405 | 65302 | 11206569 | 1556 | 0 | 0 | 3608.5496 | 3608.5496 | 3641.0904 | 90213.74 | 91027.26 | 1% | 515339.53 | 43864.95 | 892777.86 | 539794.47 | 1305565.34 | 214429.32 | 1539177.66 | 0 | 165220.37 | 1% | -332928.38 | 17672486.9
Chicago | 131 | 173354 | 165221 | 0 | 0 | 0 | 0 | 32 | 76 | 933.142 | 63404 | 11206572 | 1639 | 0 | 0 | 3608.5552 | 3608.5552 | 3641.0904 | 90213.88 | 91027.26 | 1% | 569059.86 | 43874.36 | 944603.13 | 594272.34 | 1305565.59 | 214367.95 | 1539116.54 | 0 | 165220.37 | 1% | -335806.03 | 17748957.43
Chicago | 131 | 173354 | 165221 | 0 | 0 | 0 | 0 | 159 | 2566 | 41877.049 | 1312520 | 11210406 | 1096 | 0 | 0 | 3613.6204 | 3613.6204 | 3641.0904 | 90340.51 | 91027.26 | 1% | 216416.94 | 1016200.9 | 1841075.61 | 861875.52 | 1306012.28 | 199855.16 | 1525050.44 | 0 | 165220.37 | 1% | -752491.06 | 18087788.5